## devices
device_id | manufacturer | model | description | prefix | holding_registers
[5 empty] | label | offset | bit_length | is_little_endian | is_signed | multiplier | offset_correction | data_type | min | max | units | states
[16 empty] | label | value
0 | fafeicy | WSFG-06 | Signal Generator | wsfg | voltage.peak.value | 0 | 16 | FALSE | FALSE | 0.1 | 0 | int | 1 | 24 | V
[5 empty] | frequency | 1 | 32 | FALSE | FALSE | 0.001 | 0 | int | 1 | 150 | kHz
[5 empty] | duty.cycle | 3 | 16 | FALSE | FALSE | 0.1 | 0 | int | 0 | 100 | %
[5 empty] | pulse.start.delay.time | 4 | 16 | FALSE | FALSE | 0.001 | 0 | int | 0 | 6 | s
[5 empty] | pulse.high.level.time | 5 | 16 | FALSE | FALSE | 0.001 | 0 | int | 0 | 6 | s
[5 empty] | pulse.low.level.time | 6 | 16 | FALSE | FALSE | 0.001 | 0 | int | 0 | 6 | s
[5 empty] | number.of.pulses | 7 | 16 | FALSE | FALSE | 1 | 0 | int | 0 | 60000 | pulses
[5 empty] | voltage.output | 8 | 16 | FALSE | FALSE | 0.01 | 0 | int | 0 | 10 | V
[5 empty] | voltage.output | 8 | 16 | FALSE | FALSE | 0.01 | 0 | int | 0 | 10 | V
[5 empty] | current.output | 9 | 16 | FALSE | FALSE | 0.01 | 0 | int | 0 | 20 | mA
[5 empty] | sine.wave.frequency | 10 | 16 | FALSE | FALSE | 1 | 0 | int | 0 | 1000 | Hz
[5 empty] | mode | 11 | 16 | FALSE | FALSE | 1 | 0 | int | 1 | 4 |  | PWM | 1
[16 empty] | Pulses | 2
[16 empty] | Voltage/Current Source | 3
[16 empty] | Sine Wave | 4
[5 empty] | baud.rate | 12 | 16 | FALSE | FALSE | 1 | 0 | int | 0 | 5 |  | 4800 | 0
[16 empty] | 9600 | 1
[16 empty] | 19200 | 2
[16 empty] | 38400 | 3
[16 empty] | 57600 | 4
[16 empty] | 115200 | 5
[5 empty] | output.status | 13 | 16 | FALSE | FALSE | 1 | 0 | int | 0 | 1 |  | off | 0
[16 empty] | on | 1
[5 empty] | power.on.output.status | 14 | 16 | FALSE | FALSE | 1 | 0 | int | 0 | 1 |  | invalid | 0
[16 empty] | auto-on | 1
[5 empty] | pulse.output.count | 15 | 16 | FALSE | FALSE | 1 | 0 | int | 0 | 60000
[5 empty] | number.of.pwm.pulses | 16 | 16 | FALSE | FALSE | 1 | 0 | int | 0 | 60000
1 | cummings | PowerCommand 2.x/3.x | generator set controller | PC2_3 | control.switch.position | 10 | 16 | FALSE | FALSE | 1 | 0 | int | 0 | 2 |  | off | 0
[16 empty] | auto | 1
[16 empty] | manual | 2