# PowerCommand 2.x/3.x Modbus Register Map

  - Modbus Communications

Use the following equation to calculate the value of 32-bit parameters.

    - A = high register value

    - B = low register value

parameter = (A * 65536 * multiplier) + (B * multiplier)

alternate formula: parameter = ((A*65536)+B)* multiplier

For example: Engine Running Time is a 32-bit parameter in registers 40070 and 40071.

    - Register 40070 has 322 (high register value = A).

    - Register 40071 has 15637 (low register value = B). Engine Running Time = (322 * 65536 * 0.1) + (15637 * 0.1) The engine run-time is 2111823 seconds, or 586.6 hours.

To write a 32-bit value to 2 Modbus registers, calculate the value for each register as follows:

    - A (High register value) = INT ((Parameter / Multiplier) / 65536))

    - B (Low register value) = INT ((Parameter / Multiplier) % (65536))

    - % = Modulus (the remainder of integer division)

For example: To write Load Demand Genset Run Hours = 80000.5

    - Register 40769 (high register value A) should be written to INT ((80000.5/0.1)/65536) = 12

    - Register 40770 (low register value B) should be written to INT ((80000.5/.01)%65536) = 13573

To write 32-bit values to 2 modbus addresses always write the high register value followed by the low register value. Both registers must be written to change the 32-bit value in the control.

  - Parametrics (Analog Values)

Unsupported (Not Available) Data=> "Not Available" data shall be represented as highest positive value for that parameter. For example for a two byte, unsigned integer that would be 65535. For a signed integer that would be 32767.

    - Parameters which are not available due to the sensor not being installed, or not enabled in the controllers configuration will classified like this.

Network Failed Data=> "Network Failure" data shall be represented as three less than the highest positive value for that parameter. For example for a two byte, unsigned integer that would be 65532. For a signed integer that would be 32764.

    - Data that comes from a network that has failed, such as sensors on the PCCnet I/O Module or sensor data coming in via the CAN datalink will be classified like this.

Throughout this document wherever PCC3300/PC 3.x is mentioned, it is applicable for both PCC3300V1 and PCC3300V2. Any addition related to PCC3300V2 only will be marked specifically as PCC3300V2.

NOTICE

The lowest Modbus register value is considered as the High Register Value and the highest Modbus register value is considered as the Low Register Value.

NOTICE

The Master device can read 1-40 contiguous registers, write 1-40 contiguous registers, or read diagnostic counters.

NOTICE

Hardware/Component Failure=> "Hardware/Component Failure" data shall be represented as four less than the highest positive value for that parameter. For example for a two byte, unsigned integer that would be 65531. For a signed integer that would be 32763.

    - A hardware/component failure that provides the data, such as the voltage, current and power data that comes from an external metering chip will be classified like this.

Out of Range High/Out of Range=> "Out of Range High/Out of Range" data shall be represented as one less than the highest positive value for that parameter. For example for a two byte, unsigned integer that would be 65534. For a signed integer that would be 32766.

    - Data that has been determined to be out of range high or out of range (when there is no distinction between out of range high and out of range low) due to an open sensor for example, will be classified like this.

Out of Range Low=> "Out of Range Low" data shall be represented as two less than the highest positive value for that parameter. For example for a two byte, unsigned integer that would be 65533. For a signed integer that would be 32765.

    - Data that has been determined to be out of range low due to a shorted sensor for example, will be classified like this.

If an address or bit is not listed in this table it is not implemented.

NOTICE

Earlier versions of software may not support all of the Modbus registers in the following table. If a particular register is not available in your installation, it is possible that the Modbus connection is working but the controller software does not support that particular register.

NOTICE

Data within Normal Operating Range (Valid)=> Anything other than above.

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40010 | Control Switch Position | Read Only | 0: Off 1: Auto 2: Manual | Current position of the generator set switch panel Off-Run-Auto switch as seen by the generator set control. SEE ALSO ADDRESS 40580. NOTE: Both address 40580 and 40010 show the same information however the specification for each is different. | PC 2.x, PC 3.x |
| 40011 | Genset Run Sequence State | Read Only | 0: Stop 1: Time Delay to Start 2: Warmup at Idle 3: Rated Freq and Voltage 4: Cooldown / Stop Delay 5: Cooldown at Idle 6: Rated to Idle Transition Delay | Current genset operating mode. Modbus mapping shall be in both addresses 43500 and 40011 | PC 2.x, PC3.x |
| 40012 | Most Recent Fault or Warning | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: Upper Limit: 65530 | This Modbus Register displays most recent Fault or Warning. It is not mapped with any logical. | PC 2.x, PC 3.x |
| 40013 | Modbus register 40013 | Read Only | 0: None 1: Warning 4: Shutdown | This register returns the Fault Type of the Fault Code. This is not associated with any logical. | PC 2.x |
| 40013 | Modbus register 40013 | Read Only | 0: None 1: Warning 2: Derate 3: Shutdown with Cooldown 4: Shutdown | This register returns the Fault Type of the Fault Code. This is not associated with any logical. | PC 3.x |
| 40014 | Genset % Standby Total kW | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: S Unit: % Lower Limit: Upper Limit: | Monitors the total generator set standby KW percentage output. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40016 | NFPA 110 Logical Status | Read Only | Multiplier: 1.0 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: Upper Limit: | 16-bit number to represent the status of the NFPA 110 logical. See NFPA 110 bitmap. | PC 2.x, PC 3.x |
| 40017 | Extended NFPA 110 Logical Status | Read Only | Multiplier: 1.0 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: Upper Limit: | 16-bit number to represent the status of the NFPA 110 logical. See NFPA 110 bitmap. | PC 2.x, PC 3.x |
| 40018 | Genset L1N Voltage | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit: | Generator set L1N voltage | PC 2.x, PC 3.x |
| 40019 | Genset L2N Voltage | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit: | Generator set L2N voltage | PC 2.x, PC 3.x |
| 40020 | Genset L3N Voltage | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit: | Generator set L3N voltage | PC 2.x, PC 3.x |
| 40021 | Genset LN Average Voltage | Read Only | Multiplier : 1 Offset: 0 Size (Bits) : 16 Sign: U Units: Vac Upper Limit: NA Default: 0 | Genset Line to Neutral average voltage | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40022 | Genset L1L2 Voltage | Read Only | Multiplier: 1 Lower Limit: NA Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit: | Generator set L1L2 voltage | PC 2.x, PC 3.x |
| 40023 | Genset L2L3 Voltage | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit: | Generator set L2L3 voltage | PC 2.x, PC 3.x |
| 40024 | Genset L3L1 Voltage | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit: | Generator set L3L1 voltage | PC 2.x, PC 3.x |
| 40025 | Genset LL Average Voltage | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit: | Generator set Line to Line average voltage | PC 2.x, PC 3.x |
| 40026 | Genset L1 Current | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Amps Lower Limit: Upper Limit: | Monitors the generator set L1 current value. | PC 2.x, PC 3.x |
| 40027 | Genset L2 Current | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Amps Lower Limit: Upper Limit: | Generator set L2 current | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40028 | Genset L3 Current | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Amps Lower Limit: Upper Limit: | Generator set L3 current | PC 2.x, PC 3.x |
| 40029 | Genset Average Current | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Amps Lower Limit: Upper Limit: | Generator set average current | PC 2.x, PC 3.x |
| 40030 | Genset Neutral Current | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Amps Lower Limit: Upper Limit: | Generator set neutral current | PC 3.x |
| 40031 | Genset L1 kW | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: kW Lower Limit: Upper Limit: | Generator set L1 kW | PC 2.x, PC 3.x |
| 40032 | Genset L2 kW | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: kW Lower Limit: -32768 Upper Limit: 32762 | Generator set L2 kW | PC 2.x, PC 3.x |
| 40033 | Genset L3 kW | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: kW Lower Limit: -32768 Upper Limit: 32762 | Generator set L3 kW | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40034 | Genset Total kW | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: kW Lower Limit: Upper Limit: | Generator set total kW | PC 2.x, PC 3.x |
| 40035 | Genset L1 kVAR | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: kVAR Lower Limit: Upper Limit: | Generator set L1 kVAR | PC 2.x, PC 3.x |
| 40036 | Genset L2 kVAR | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: kVAR Lower Limit: -32768 Upper Limit: 32762 | Generator set L2 kVAR | PC 2.x, PC 3.x |
| 40037 | Genset L3 kVAR | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: kVAR Lower Limit: Upper Limit | Generator set L3 kVAR | PC 2.x, PC 3.x |
| 40038 | Genset Total kVAR | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: kVAR Lower Limit: Upper Limit | Generator set total kVAR | PC 2.x, PC 3.x |
| 40039 | Genset Total Power Factor | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 8 Sign: S Unit: PF Lower Limit: Upper Limit | Generator set total power factor (L1+L2+L3) | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40040 | Genset L1 kVA | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: kVA Lower Limit: Upper Limit | Generator set L1 kVA | PC 2.x, PC 3.x |
| 40041 | Genset L2 kVA | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: kVA Lower Limit: Upper Limit | Generator set L2 kVA | PC 2.x, PC 3.x |
| 40042 | Genset L3 kVA | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit kVA Lower Limit: Upper Limit | Generator set L3 kVA | PC 2.x, PC 3.x |
| 40043 | Genset Total kVA | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: kVA Lower Limit: Upper Limit | Generator set total kVA | PC 2.x, PC 3.x |
| 40044 | Genset Frequency OP | Read Only | Multiplier : 0.01 Offset: 0 Size (bits): 16 Sign: U Unit: Hz Lower Limit: NA Upper Limit: NA | Genset Frequency OP. Modbus has different multiplier than PCCnet. For Modbus use only, Multiplier/Units = 0.1 Hz | PC 2.X, PC 3.X |
| 40046 | Genset Total Negative kWh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: kWh Lower Limit: Upper Limit: | Generator set total negative kWh accumulation | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40047 | Genset Total Negative kWh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: kWh Lower Limit: Upper Limit: | Generator set total negative kWh accumulation | PC 2.x, PC 3.x |
| 40048 | Genset Total Positive kWh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: kWh Lower Limit: 0 Upper Limit: 4294967290 | Generator set total positive kWh accumulation | PC 2.x, PC 3.x |
| 40049 | Genset Total Positive kWh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: kWh Lower Limit: 0 Upper Limit: 4294967290 | Generator set total positive kWh accumulation | PC 2.x, PC 3.x |
| 40050 | Genset Total Net kWh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: S Unit: kWh Lower Limit: -2147483648 Upper Limit: 2147483643 | Generator set total net kWh accumulation | PC 2.x, PC 3.x |
| 40051 | Genset Total Net kWh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: S Unit: kWh Lower Limit: -2147483648 Upper Limit: 2147483643 | Generator set total net kWh accumulation | PC 2.x, PC 3.x |
| 40052 | Genset Total Negative kVARh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: kVARh Lower Limit: Upper Limit: | Generator set total negative kVARh accumulation | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40053 | Genset Total Negative kVARh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: kVARh Lower Limit: Upper Limit: | Generator set total negative kVARh accumulation | PC 2.x, PC 3.x |
| 40054 | Genset Total Positive kVARh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: kVARh Lower Limit: 0 Upper Limit: 4294967290 | Generator set total positive kVARh accumulation | PC 2.x, PC 3.x |
| 40055 | Genset Total Positive kVARh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: kVARh Lower Limit: 0 Upper Limit: 4294967290 | Generator set total positive kVARh accumulation | PC 2.x, PC 3.x |
| 40056 | Genset Total Net kVARh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: S Unit: kVARh Lower Limit: -2147483648 Upper Limit: 2147483643 | Generator set total net kVARh accumulation | PC 2.x, PC 3.x |
| 40057 | Generator set Total Net kVARh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: S Unit: kVARh Lower Limit: -2147483648 Upper Limit: 2147483643 | Generator set total net kVARh accumulation | PC 2.x, PC 3.x |
| 40058 | Genset % Standby L1 Current | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: % Lower Limit: Upper Limit: | Monitors the generator set standby L1 current percentage output. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40059 | Genset % Standby L2 Current | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: % Lower Limit: Upper Limit: | Monitors the generator set standby L2 current percentage output. | PC 2.x, PC 3.x |
| 40060 | Genset % Standby L3 Current | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: % Lower Limit: Upper Limit: | Monitors the generator set standby L3 current percentage output. | PC 2.x, PC 3.x |
| 40061 | Battery Voltage | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Vdc Lower Limit: Upper Limit: | Battery voltage value. Modbus and PCCNet has different multiplier value. For Modbus use only, multiplier/units = 0.1 volts | PC 2.x, PC 3.x |
| 40062 | Oil Pressure | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: kPa Lower Limit: Upper Limit: | Monitor point for the Oil Pressure. Modbus and PCCNet have different multiplier value. For Modbus use only, Multiplier/Units = 1kPa | PC 2.x, PC 3.x |
| 40063 | Oil Temperature | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: Upper Limit: | Monitor point for the Oil Temperature | PC 2.x, PC 3.x |
| 40064 | Coolant Temperature | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degC Lower Limit: Upper Limit: | Monitor point for the Coolant Temperature. Modbus mapping shall be to both 46126 and 40064 addresses. For Modbus use only, Multiplier/Units = 0.1C | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40065 | Intake Manifold Temperature | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: -40 Upper Limit: 410 | To monitor Intake Manifold Temperature. This parameter represents ”Intake Manifold Temperature 1”. | PC 2.x, PC 3.x |
| 40065 | Intake Manifold Temperature | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: -40 Upper Limit: 410 | To monitor Intake Manifold Temperature. This parameter represents ”Intake Manifold Temperature 1”. | PC 2.x, PC 3.x |
| 40066 | Fuel Temperature | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: -40 Upper Limit: 410 | Monitor point for the Fuel Temperature | PC 2.x, PC 3.x |
| 40067 | Fuel Rate | Read Only | Multiplier: 0.05 Offset: 0 Size (bits): 16 Sign: S Unit: gal/hr Lower Limit: Upper Limit: | Monitor point for the Fuel Rate | PC 2.x, PC 3.x |
| 40068 | Average Engine Speed | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: RPM Lower Limit: Upper Limit: | Monitor point for the Average Engine Speed. Modbus and PCCNet have different multiplier value. For Modbus use only, Multiplier/Units = 1 RPM | PC 2.x, PC 3.x |
| 40069 | Total Start Attempts OP | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Unit: NAr Lower Limit: 0 Upper Limit: 65535 | Total number of start attempts | PC 2.X, PC3.X |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40070 | Engine Running Time | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 32 Sign: U Unit: seconds Lower Limit: Upper Limit: | Total engine run time. Modbus has different multiplier than PCCNet. For Modbus use only, multiplier/units = 0.1 Sec | PC 2.x, PC 3.x |
| 40071 | Engine Running Time | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 32 Sign: U Unit: seconds Lower Limit: Upper Limit: | Total engine run time. Modbus has different multiplier than PCCnet. For Modbus use only, multiplier/units = 0.1 Sec | PC 2.x, PC 3.x |
| 40072 | Total Fuel Consumption | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 32 Sign: U Unit: gallons Lower Limit: Upper Limit: | Total fuel consumption since start of engine. | PC 2.x, PC 3.x |
| 40073 | Total Fuel Consumption | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 32 Sign: U Unit: gallons Lower Limit: Upper Limit: | Total fuel consumption since start of engine. | PC 2.x, PC 3.x |
| 40074 | Total Number of Runs | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: Lower Limit: 0 Upper Limit: 4294967295 | Total number of generator set runs. | PC 2.x, PC 3.x |
| 40075 | Total Number of Runs | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: Lower Limit: 0 Upper Limit: 4294967295 | Total number of generator set runs. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40076 | Runs Reset Time | Read Only | Multiplier: 1 Offset: 0 Size (bits): 144 Sign: C Unit: Lower Limit: Upper Limit: | Real Time Clock stamp record of the last time the Run Attempts were reset. This parameter is READ/WRITE for Mon and PCCNet and READ ONLY for Modbus. Modbus implementation or the Real time stamp will use 40076- 40092 for 17 char of this string. | PC 2.x, PC 3.x |
| 40077 | Runs Reset Time | Read Only | Multiplier: 1 Offset: 0 Size (bits): 144 Sign: C Unit: Lower Limit: Upper Limit: | Real Time Clock stamp record of the last time the Run Attempts were reset. This parameter is READ/WRITE for Mon and PCCNet and READ ONLY for Modbus. Modbus implementation or the Real time stamp will use 40076- 40092 for 17 char of this string. | PC 2.x, PC 3.x |
| 40078 | Runs Reset Time | Read Only | Multiplier: 1 Offset: 0 Size (bits): 144 Sign: C Unit: Lower Limit: Upper Limit: | Real Time Clock stamp record of the last time the Run Attempts were reset. This parameter is READ/WRITE for Mon and PCCNet and READ ONLY for Modbus. Modbus implementation or the Real time stamp will use 40076 - 40092 for 17 char of this string. | PC 2.x, PC 3.x |
| 40079 | Runs Reset Time | Read Only | Multiplier: 1 Offset: 0 Size (bits): 144 Sign: C Unit: Lower Limit: Upper Limit: | Real Time Clock stamp record of the last time the Run Attempts were reset. This parameter is READ/WRITE for Mon and PCCNet and READ ONLY for Modbus. Modbus implementation or the Real time stamp will use 40076- 40092 for 17 char of this string. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40080 | Runs Reset Time | Read Only | Multiplier: 1 Offset: 0 Size (bits): 144 Sign: C Unit: Lower Limit: Upper Limit: | Real Time Clock stamp record of the last time the Run Attempts were reset. This parameter is READ/WRITE for Mon and PCCNet and READ ONLY for Modbus. Modbus implementation or the Real time stamp will use 40076- 40092 for 17 char of this string. | PC 2.x, PC 3.x |
| 40081 | Runs Reset Time | Read Only | Multiplier: 1 Offset: 0 Size (bits): 144 Sign: C Unit: Lower Limit: Upper Limit: | Real Time Clock stamp record of the last time the Run Attempts were reset. This parameter is READ/WRITE for Mon and PCCNet and READ ONLY for Modbus. Modbus implementation or the Real time stamp will use 40076- 40092 for 17 char of this string. | PC 2.x, PC 3.x |
| 40082 | Runs Reset Time | Read Only | Multiplier: 1 Offset: 0 Size (bits): 144 Sign: C Unit: Lower Limit: Upper Limit: | Real Time Clock stamp record of the last time the Run Attempts were reset. This parameter is READ/WRITE for Mon and PCCNet and READ ONLY for Modbus. Modbus implementation or the Real time stamp will use 40076- 40092 for 17 char of this string. | PC 2.x, PC 3.x |
| 40083 | Runs Reset Time | Read Only | Multiplier: 1 Offset: 0 Size (bits): 144 Sign: C Unit: Lower Limit: Upper Limit: | Real Time Clock stamp record of the last time the Run Attempts were reset. This parameter is READ/WRITE for Mon and PCCNet and READ ONLY for Modbus. Modbus implementation or the Real time stamp will use 40076- 40092 for 17 char of this string. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40084 | Runs Reset Time | Read Only | Multiplier: 1 Offset: 0 Size (bits): 144 Sign: C Unit: Lower Limit: Upper Limit: | Real Time Clock stamp record of the last time the Run Attempts were reset. This parameter is READ/WRITE for Mon and PCCNet and READ ONLY for Modbus. Modbus implementation or the Real time stamp will use 40076- 40092 for 17 char of this string. | PC 2.x, PC 3.x |
| 40085 | Runs Reset Time | Read Only | Multiplier: 1 Offset: 0 Size (bits): 144 Sign: C Unit: Lower Limit: Upper Limit: | Real Time Clock stamp record of the last time the Run Attempts were reset. This parameter is READ/WRITE for Mon and PCCNet and READ ONLY for Modbus. Modbus implementation or the Real time stamp will use 40076- 40092 for 17 char of this string. | PC 2.x, PC 3.x |
| 40086 | Runs Reset Time | Read Only | Multiplier: 1 Offset: 0 Size (bits): 144 Sign: C Unit: Lower Limit: Upper Limit: | Real Time Clock stamp record of the last time the Run Attempts were reset. This parameter is READ/WRITE for Mon and PCCNet and READ ONLY for Modbus. Modbus implementation or the Real time stamp will use 40076- 40092 for 17 char of this string. | PC 2.x, PC 3.x |
| 40087 | Runs Reset Time | Read Only | Multiplier: 1 Offset: 0 Size (bits): 144 Sign: C Unit: Lower Limit: Upper Limit: | Real Time Clock stamp record of the last time the Run Attempts were reset. This parameter is READ/WRITE for Mon and PCCNet and READ ONLY for Modbus. Modbus implementation or the Real time stamp will use 40076- 40092 for 17 char of this string. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40088 | Runs Reset Time | Read Only | Multiplier: 1 Offset: 0 Size (bits): 144 Sign: C Unit: Lower Limit: Upper Limit: | Real Time Clock stamp record of the last time the Run Attempts were reset. This parameter is READ/WRITE for Mon and PCCNet and READ ONLY for Modbus. Modbus implementation or the Real time stamp will use 40076- 40092 for 17 char of this string. | PC 2.x, PC 3.x |
| 40089 | Runs Reset Time | Read Only | Multiplier: 1 Offset: 0 Size (bits): 144 Sign: C Unit: Lower Limit: Upper Limit: | Real Time Clock stamp record of the last time the Run Attempts were reset. This parameter is READ/WRITE for Mon and PCCNet and READ ONLY for Modbus. Modbus implementation or the Real time stamp will use 40076- 40092 for 17 char of this string. | PC 2.x, PC 3.x |
| 40090 | Runs Reset Time | Read Only | Multiplier: 1 Offset: 0 Size (bits): 144 Sign: C Unit: Lower Limit: Upper Limit: | Real Time Clock stamp record of the last time the Run Attempts were reset. This parameter is READ/WRITE for Mon and PCCNet and READ ONLY for Modbus. Modbus implementation or the Real time stamp will use 40076- 40092 for 17 char of this string. | PC 2.x, PC 3.x |
| 40091 | Runs Reset Time | Read Only | Multiplier: 1 Offset: 0 Size (bits): 144 Sign: C Unit: Lower Limit: Upper Limit: | Real Time Clock stamp record of the last time the Run Attempts were reset. This parameter is READ/WRITE for Mon and PCCNet and READ ONLY for Modbus. Modbus implementation or the Real time stamp will use 40076- 40092 for 17 char of this string. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40092 | Runs Reset Time | Read Only | Multiplier: 1 Offset: 0 Size (bits): 144 Sign: C Unit: Lower Limit: Upper Limit: | Real Time Clock stamp record of the last time the Run Attempts were reset. This parameter is READ/WRITE for Mon and PCCNet and READ ONLY for Modbus. Modbus implementation or the Real time stamp will use 40076- 40092 for 17 char of this string. | PC 2.x, PC 3.x |
| 40096 | Start Attempts Reset Time | Read Only | Multiplier: 1 Offset: 0 Size (bits): 144 Sign: C Unit: Lower Limit: Upper Limit: | Real Time Clock stamp record of the last time the Start Attempts were reset. This parameter is READ/WRITE for Mon and PCCNet and READ ONLY for Modbus. Modbus implementation or the Real time stamp will use 40096- 0112 for 17 char of this string. | PC 2.x, PC 3.x |
| 40097 | Start Attempts Reset Time | Read Only | Multiplier: 1 Offset: 0 Size (bits): 144 Sign: C Unit: Lower Limit: Upper Limit: | Real Time Clock stamp record of the last time the Start Attempts were reset. This parameter is READ/WRITE for Mon and PCCNet and READ ONLY for Modbus. Modbus implementation or the Real time stamp will use 40096- 0112 for 17 char of this string. | PC 2.x, PC 3.x |
| 40098 | Start Attempts Reset Time | Read Only | Multiplier: 1 Offset: 0 Size (bits): 144 Sign: C Unit: Lower Limit: Upper Limit: | Real Time Clock stamp record of the last time the Start Attempts were reset. This parameter is READ/WRITE for Mon and PCCNet and READ ONLY for Modbus. Modbus implementation or the Real time stamp will use 40096- 0112 for 17 char of this string. | PC 2.x, PC 3.x |
| 40099 | Start Attempts Reset Time | Read Only | Multiplier: 1 Offset: 0 Size (bits): 144 Sign: C Unit: Lower Limit: Upper Limit: | Real Time Clock stamp record of the last time the Start Attempts were reset. This parameter is READ/WRITE for Mon and PCCNet and READ ONLY for Modbus. Modbus implementation or the Real time stamp will use 40096- 0112 for 17 char of this string. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40100 | Start Attempts Reset Time | Read Only | Multiplier: 1 Offset: 0 Size (bits): 144 Sign: C Unit: Lower Limit: Upper Limit: | Real Time Clock stamp record of the last time the Start Attempts were reset. This parameter is READ/WRITE for Mon and PCCNet and READ ONLY for Modbus. Modbus implementation or the Real time stamp will use 40096- 0112 for 17 char of this string. | PC 2.x, PC 3.x |
| 40101 | Start Attempts Reset Time | Read Only | Multiplier: 1 Offset: 0 Size (bits): 144 Sign: C Unit: Lower Limit: Upper Limit: | Real Time Clock stamp record of the last time the Start Attempts were reset. This parameter is READ/WRITE for Mon and PCCNet and READ ONLY for Modbus. Modbus implementation or the Real time stamp will use 40096- 0112 for 17 char of this string. | PC 2.x, PC 3.x |
| 40102 | Start Attempts Reset Time | Read Only | Multiplier: 1 Offset: 0 Size (bits): 144 Sign: C Unit: Lower Limit: Upper Limit: | Real Time Clock stamp record of the last time the Start Attempts were reset. This parameter is READ/WRITE for Mon and PCCNet and READ ONLY for Modbus. Modbus implementation or the Real time stamp will use 40096- 0112 for 17 char of this string. | PC 2.x, PC 3.x |
| 40103 | Start Attempts Reset Time | Read Only | Multiplier: 1 Offset: 0 Size (bits): 144 Sign: C Unit: Lower Limit: Upper Limit: | Real Time Clock stamp record of the last time the Start Attempts were reset. This parameter is READ/WRITE for Mon and PCCNet and READ ONLY for Modbus. Modbus implementation or the Real time stamp will use 40096- 0112 for 17 char of this string. | PC 2.x, PC 3.x |
| 40104 | Start Attempts Reset Time | Read Only | Multiplier: 1 Offset: 0 Size (bits): 144 Sign: C Unit: Lower Limit: Upper Limit: | Real Time Clock stamp record of the last time the Start Attempts were reset. This parameter is READ/WRITE for Mon and PCCNet and READ ONLY for Modbus. Modbus implementation or the Real time stamp will use 40096- 0112 for 17 char of this string. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40105 | Start Attempts Reset Time | Read Only | Multiplier: 1 Offset: 0 Size (bits): 144 Sign: C Unit: Lower Limit: Upper Limit: | Real Time Clock stamp record of the last time the Start Attempts were reset. This parameter is READ/WRITE for Mon and PCCNet and READ ONLY for Modbus. Modbus implementation or the Real time stamp will use 40096- 0112 for 17 char of this string. | PC 2.x, PC 3.x |
| 40106 | Start Attempts Reset Time | Read Only | Multiplier: 1 Offset: 0 Size (bits): 144 Sign: C Unit: Lower Limit: Upper Limit: | Real Time Clock stamp record of the last time the Start Attempts were reset. This parameter is READ/WRITE for Mon and PCCNet and READ ONLY for Modbus. Modbus implementation or the Real time stamp will use 40096- 0112 for 17 char of this string. | PC 2.x, PC 3.x |
| 40107 | Start Attempts Reset Time | Read Only | Multiplier: 1 Offset: 0 Size (bits): 144 Sign: C Unit: Lower Limit: Upper Limit: | Real Time Clock stamp record of the last time the Start Attempts were reset. This parameter is READ/WRITE for Mon and PCCNet and READ ONLY for Modbus. Modbus implementation or the Real time stamp will use 40096- 0112 for 17 char of this string. | PC 2.x, PC 3.x |
| 40108 | Start Attempts Reset Time | Read Only | Multiplier: 1 Offset: 0 Size (bits): 144 Sign: C Unit: Lower Limit: Upper Limit: | Real Time Clock stamp record of the last time the Start Attempts were reset. This parameter is READ/WRITE for Mon and PCCNet and READ ONLY for Modbus. Modbus implementation or the Real time stamp will use 40096- 0112 for 17 char of this string. | PC 2.x, PC 3.x |
| 40109 | Start Attempts Reset Time | Read Only | Multiplier: 1 Offset: 0 Size (bits): 144 Sign: C Unit: Lower Limit: Upper Limit: | Real Time Clock stamp record of the last time the Start Attempts were reset. This parameter is READ/WRITE for Mon and PCCNet and READ ONLY for Modbus. Modbus implementation or the Real time stamp will use 40096- 0112 for 17 char of this string. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40110 | Start Attempts Reset Time | Read Only | Multiplier: 1 Offset: 0 Size (bits): 144 Sign: C Unit: Lower Limit: Upper Limit: | Real Time Clock stamp record of the last time the Start Attempts were reset. This parameter is READ/WRITE for Mon and PCCNet and READ ONLY for Modbus. Modbus implementation or the Real time stamp will use 40096- 0112 for 17 char of this string. | PC 2.x, PC 3.x |
| 40111 | Start Attempts Reset Time | Read Only | Multiplier: 1 Offset: 0 Size (bits): 144 Sign: C Unit: Lower Limit: Upper Limit: | Real Time Clock stamp record of the last time the Start Attempts were reset. This parameter is READ/WRITE for Mon and PCCNet and READ ONLY for Modbus. Modbus implementation or the Real time stamp will use 40096- 0112 for 17 char of this string. | PC 2.x, PC 3.x |
| 40112 | Start Attempts Reset Time | Read Only | Multiplier: 1 Offset: 0 Size (bits): 144 Sign: C Unit: Lower Limit: Upper Limit: | Real Time Clock stamp record of the last time the Start Attempts were reset. This parameter is READ/WRITE for Mon and PCCNet and READ ONLY for Modbus. Modbus implementation or the Real time stamp will use 40096- 0112 for 17 char of this string. | PC 2.x, PC 3.x |
| 40118 | Utility L1N Voltage | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit: | Utility L1N voltage | PC 3.x |
| 40119 | Utility L2N Voltage | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit: | Utility L2N voltage | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40120 | Utility L3N Voltage | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit: | Utility L3N voltage | PC 3.x |
| 40121 | Utility LN Average Voltage | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: NA Upper Limit: NA | Utility Line to Neutral average voltage | PC3.X |
| 40122 | Utility L1L2 Voltage | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit: | Utility L1L2 voltage | PC 3.x |
| 40123 | Utility L2L3 Voltage | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit: | Utility L2L3 voltage | PC 3.x |
| 40124 | Utility L3L1 Voltage | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit: | Utility L3L1 voltage | PC 3.x |
| 40125 | Utility LL Average Voltage | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit: | Utility Line to Line average voltage | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40126 | Utility L1 Current | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Amps Lower Limit: Upper Limit: | Utility L1 current | PC 3.x |
| 40127 | Utility L2 Current | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Amps Lower Limit: Upper Limit: | Utility L2 current | PC 3.x |
| 40128 | Utility L3 Current | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Amps Lower Limit: Upper Limit: Offset: 0 | Utility L3 current | PC 3.x |
| 40129 | Utility Average Current | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Unit: Amps Lower Limit: NA Upper Limit: NA Default: NA | Utility average current | PC 3.x |
| 40131 | Utility L1 kW | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: kW Lower Limit: Upper Limit: | Utility L1 kW | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40132 | Utility L2 kW | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: kW Lower Limit: Upper Limit: | Utility L2 kW | PC 3.x |
| 40133 | Utility L3 kW | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: kW Lower Limit: Upper Limit: | Utility L3 kW | PC 3.x |
| 40134 | Utility Total kW | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: kW Lower Limit: Upper Limit: | Utility total kW | PC 3.x |
| 40135 | Utility L1 kVAR | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: kVAR Lower Limit: Upper Limit: | Utility L1 kVAR | PC 3.x |
| 40136 | Utility L2 kVAR | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: kVAR Lower Limit: Upper Limit: | Utility L2 kVAR | PC 3.x |
| 40137 | Utility L3 kVAR | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: kVAR Lower Limit: Upper Limit: | Utility L3 kVAR | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40138 | Utility Total kVAR | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: kVAR Lower Limit: Upper Limit: | Utility total kVAR | PC 3.x |
| 40139 | Utility Total Power Factor | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 8 Sign: S Unit: PF Lower Limit: Upper Limit: | Utility total power factor | PC 3.x |
| 40140 | Utility L1 kVA | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: kVA Lower Limit: Upper Limit: | Utility L1 kVA | PC 3.x |
| 40141 | Utility L2 kVA | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: kVA Lower Limit: Upper Limit: | Utility L2 kVA | PC 3.x |
| 40142 | Utility L3 kVA | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: kVA Lower Limit: Upper Limit: | Utility L3 kVA | PC 3.x |
| 40143 | Utility Total kVA | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: kVA Lower Limit: Upper Limit: | Utility total kVA | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40144 | Utility Frequency | Read Only | Multiplier: 0.001 Offset: 0 Size (bits): 32 Sign: U Unit: Hz Lower Limit: Upper Limit: | Utility line frequency | PC 3.x |
| 40145 | Utility Frequency | Read Only | Multiplier: 0.001 Offset: 0 Size (bits): 32 Sign: U Unit: Hz Lower Limit: Upper Limit: | Utility line frequency | PC 3.x |
| 40146 | Utility Total Negative kWh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: kWh Lower Limit: Upper Limit: | Utility total negative kWh accumulation | PC 3.x |
| 40147 | Utility Total Negative kWh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: kWh Lower Limit: Upper Limit: | Utility total negative kWh accumulation | PC 3.x |
| 40148 | Utility Total Positive kWh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: kWh Lower Limit: Upper Limit: | Utility total positive kWh accumulation | PC 3.x |
| 40149 | Utility Total Positive kWh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: kWh Lower Limit: Upper Limit: | Utility total positive kWh accumulation | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40150 | Utility Total Net kWh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: S Unit: kWh Lower Limit: Upper Limit: | Utility total net kWh accumulation | PC 3.x |
| 40151 | Utility Total Net kWh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: S Unit: kWh Lower Limit: Upper Limit: | Utility total net kWh accumulation | PC 3.x |
| 40152 | Utility Total Negative kVARh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: kVARh Lower Limit: Upper Limit: | Utility total negative kVARh accumulation | PC 3.x |
| 40153 | Utility Total Negative kVARh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: kVARh Lower Limit: Upper Limit: | Utility total negative kVARh accumulation | PC 3.x |
| 40154 | Utility Total Positive kVARh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: kVARh Lower Limit: Upper Limit: | Utility total positive kVARh accumulation | PC 3.x |
| 40155 | Utility Total Positive kVARh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: kVARh Lower Limit: Upper Limit: | Utility total positive kVARh accumulation | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40156 | Utility Total Net kVARh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: S Unit: kVARh Lower Limit: Upper Limit: | Utility total net kVARh accumulation | PC 3.x |
| 40157 | Utility Total Net kVARh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: S Unit: kVARh Lower Limit: Upper Limit: | Utility total net kVARh accumulation | PC 3.x |
| 40158 | Genset Bus L1N Voltage | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit: | Generator set Bus L1N voltage | PC 3.x |
| 40159 | Genset Bus L2N Voltage | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit: | Generator set Bus L2N voltage | PC 3.x |
| 40160 | Genset Bus L3N Voltage | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit: | Generator set Bus L3N voltage | PC 3.x |
| 40161 | Genset Bus LN Average Voltage | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit: | Genset Bus Line to Neutral average voltage | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40162 | Genset Bus L1L2 Voltage | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit: | Generator set Bus L1L2 voltage | PC 3.x |
| 40163 | Genset Bus L2L3 Voltage | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit: | Generator set Bus L2L3 voltage | PC 3.x |
| 40164 | Genset Bus L3L1 Voltage | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit: | Generator set Bus L3L1 voltage | PC 3.x |
| 40165 | Genset Bus LL Average Voltage | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit: | Generator set Bus Line to Line average voltage | PC 3.x |
| 40166 | Genset Bus L1 Current | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Amps Lower Limit: 0 Upper Limit: 65530 | Generator set Bus L1 current | PC 3.x |
| 40167 | Genset Bus L2 Current | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Amps Lower Limit: Upper Limit: | Generator set Bus L2 current | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40168 | Genset Bus L3 Current | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Amps Lower Limit: Upper Limit: | Generator set Bus L3 current | PC 3.x |
| 40169 | Genset Bus Average Current | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Unit: Amps Lower Limit: NA Upper Limit: NA | Genset Bus Average current | PC3.X |
| 40171 | Genset Bus L1 kW | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: kW Lower Limit: -32768 Upper Limit: 32762 | Generator set Bus L1 kW | PC 3.x |
| 40172 | Genset Bus L2 kW | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: kW Lower Limit: -32768 Upper Limit: 32762 | Generator set Bus L2 kW | PC 3.x |
| 40173 | Genset Bus L3 kW | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: kW Lower Limit: Upper Limit: | Generator set Bus L3 kW | PC 3.x |
| 40174 | Genset Bus Total kW | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: kW Lower Limit: Upper Limit: | Generator set Bus total kW | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40175 | Genset Bus L1 kVAR | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: kVAR Lower Limit: -32678 Upper Limit: 32672 | Generator set bus L1 kVar | PC 3.x |
| 40176 | Genset Bus L2 kVAR | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: kVAR Lower Limit: -32678 Upper Limit: 32672 | Generator set bus L2 kVAR | PC 3.x |
| 40177 | Genset Bus L3 kVAR | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: kVAR Lower Limit: Upper Limit: | Generator set bus L3 kVAR | PC 3.x |
| 40178 | Genset Bus Total kVAR | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: kVAR Lower Limit: Upper Limit: | Generator set bus total kVAR | PC 3.x |
| 40179 | Genset Bus Total Power Factor | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 8 Sign: S Unit: PF Lower Limit: Upper Limit: | Generator set Bus Total power factor | PC 3.x |
| 40180 | Genset Bus L1 kVA | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: kVA Lower Limit: Upper Limit: | Generator set Bus L1 kVA | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40181 | Genset Bus L2 kVA | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: kVA Lower Limit: Upper Limit: | Generator set Bus L2 kVA | PC 3.x |
| 40182 | Genset Bus L3 kVA | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: kVA Lower Limit: Upper Limit: | Generator set Bus L3 kVA | PC 3.x |
| 40183 | Genset Bus Total kVA | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: kVA Lower Limit: Upper Limit: | Generator set bus total kVA | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40184 | Genset Bus Frequency | Read Only | Multiplier: 0.001 Offset: 0 Size (bits): 32 Sign: U Unit: Hz Lower Limit: Upper Limit: | Generator set bus line frequency | PC 3.x |
| 40185 | Genset Bus Frequency | Read Only | Multiplier: 0.001 Offset: 0 Size (bits): 32 Sign: U Unit: Hz Lower Limit: Upper Limit: | Generator set bus line frequency | PC 3.x |
| 40186 | Genset Bus Total Negative kWh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: kWh Lower Limit: Upper Limit: | Generator set bus total negative kWh accumulation | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40187 | Genset Bus Total Negative kWh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: kWh Lower Limit: Upper Limit: | Generator set bus total negative kWh accumulation | PC 3.x |
| 40188 | Genset Bus Total Positive kWh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: kWh Lower Limit: Upper Limit: | Generator set bus total positive kWh accumulation | PC 3.x |
| 40189 | Genset Bus Total Positive kWh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: kWh Lower Limit: Upper Limit: | Generator set bus total positive kWh accumulation | PC 3.x |
| 40190 | Genset Bus Total Net kWh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: S Unit: kWh Lower Limit: Upper Limit: | Generator set bus total net kWh accumulation | PC 3.x |
| 40191 | Genset Bus Total Net kWh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: S Unit: kWh Lower Limit: Upper Limit: | Generator set bus total net kWh accumulation | PC 3.x |
| 40192 | Genset Bus Total Negative kVARh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: kVARh Lower Limit: Upper Limit: | Generator set bus total negative kVARh accumulation | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40193 | Genset Bus Total Negative kVARh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: kVARh Lower Limit: Upper Limit: | Generator set bus total negative kVARh accumulation | PC 3.x |
| 40194 | Genset Bus Total Positive kVARh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: kVARh Lower Limit: Upper Limit: | Generator set bus total positive kVARh accumulation | PC 3.x |
| 40195 | Genset Bus Total Positive kVARh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: kVARh Lower Limit: Upper Limit: | Generator set bus total positive kVARh accumulation | PC 3.x |
| 40196 | Genset Bus Total Net kVARh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: S Unit: kVARh Lower Limit: Upper Limit: | Generator set Bus total net kVARh accumulation | PC 3.x |
| 40197 | Genset Bus Total Net kVARh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: S Unit: kVARh Lower Limit: Upper Limit: | Generator set Bus total net kVARh accumulation | PC 3.x |
| 40198 | Ground Current | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: amp Lower Limit: Upper Limit: | Ground current | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40199 | Genset Negative Sequence Current % | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: U Unit: % Lower Limit: Upper Limit: | Generator set Negative Sequence Current as Percent of Standby Current Rating | PC 3.x |
| 40201 | Coolant Temperature Sensor Type | Read Only | 0: PGBU 1: EBU | Either PGBU(Onan) or EBU(Cummins) sensor. | PC 2.x, PC 3.x |
| 40207 | Battery Charger Alternator Flash Voltage | Read Only | Multiplier: 0.001 Offset: 0 Size (bits): 16 Sign: U Unit: Vdc Lower Limit: 0 Upper Limit: 35 | The Battery Charger Alternator Flash Voltage after all scaling and validity checks. | PC 2.x, PC 3.x |
| 40208 | Battery 1 Voltage (Aux101) | Read Only | Multiplier : 0.01 Offset: 0 Size (bits): 16 Sign: U Unit: Vdc Lower Limit: 0 Upper Limit: 3850 Default: NA | Battery 1 Voltage measured through AUX101. Applicable when multiple batteries are used. | PC 3.x |
| 40209 | Battery 2 Voltage (Aux101) | Read Only | Multiplier : 0.01 Offset: 0 Size (bits): 16 Sign: U Unit: Vdc Lower Limit: 0 Upper Limit: 3850 Default: NA | Battery 2 Voltage measured through AUX101. Applicable when multiple batteries are used. | PC 3.x |
| 40210 | External Speed Bias Input | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: S Unit: % Lower Limit: -100 Upper Limit: 100 | Monitor point for the external speed bias input. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40211 | External Voltage Bias Input | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: S Unit: % Lower Limit: -100 Upper Limit: 100 | Monitor point for the external voltage bias input. | PC 2.x, PC 3.x |
| 40212 | Battery 3 Voltage (Aux101) | Read Only | Multiplier : 0.01 Offset: 0 Size (bits): 16 Sign: U Unit: Vdc Lower Limit: 0 Upper Limit: 3850 Default: NA | Battery 3 Voltage measured through AUX101. Applicable when multiple batteries are used. | PC 3.x |
| 40213 | Battery 4 Voltage (Aux101) | Read Only | Multiplier : 0.01 Offset: 0 Size (bits): 16 Sign: U Unit: Vdc Lower Limit: 0 Upper Limit: 3850 Default: NA | Battery 4 Voltage measured through AUX101. Applicable when multiple batteries are used. | PC 3.x |
| 40214 | kVAR Load Setpoint | Read Only | Multiplier : 0.01 Offset: 0 Size (bits): 16 Sign: S Unit: % Lower Limit: NA Upper Limit: NA Default: NA | EU scaled value for the kVAR load setpoint | PC 3.x |
| 40217 | kVAR Load Share Level | Read Only | Multiplier : 0.01 Offset: 0 Size (bits): 16 Sign: S Unit: % Lower Limit: NA Upper Limit: NA Default: NA | EU Scaled value for the kVAR load share level analog input | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40219 | kW load setpoint | Read Only | Multiplier : 0.01 Offset: 0 Size (bits): 16 Sign: S Unit: % Lower Limit: Upper Limit: 125.01 Default: NA | EU scaled value for the kW load setpoint | PC 3.x |
| 40222 | kW Load Share Level | Read Only | Multiplier : 0.01 Offset: 0 Size (bits): 16 Sign: S Unit: % Lower Limit: NA Upper Limit: NA Default: NA | EU Scaled value for the kW load share level analog input | PC 3.x |
| 40224 | kVAR Load Share Output Predictor | Read Only | Multiplier : 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: uA Lower Limit: NA Upper Limit: NA Default: NA | uA signal being injected into a 10K ohm resistor network | PC 3.x |
| 40225 | KW Load Share Output Predictor | Read Only | Multiplier : 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: uA Lower Limit: NA Upper Limit: NA Default: NA | uA signal being injected into a 10K ohm resistor network | PC 3.x |
| 40226 | Speed Bias Output / Configurable Analog output #1 Output Predictor | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: S Unit: Vdc Lower Limit: NA Upper Limit: NA | Configurable analog output voltage output value (predicted) | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40227 | Voltage Bias Output / Configurable Analog output #2 Output Predictor | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: S Unit: Vdc Lower Limit: Upper Limit: | Configurable analog output voltage output value (predicted) | PC 3.x |
| 40228 | Amber Warning Lamp Status | Read Only | 0: Inactive 1: Active | Engine Control System indicates a warning condition. | PC 2.x, PC 3.x |
| 40229 | Barometric Absolute Pressure | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: psi Lower Limit: Upper Limit: | Monitor point for the Barometric Absolute Pressure. Displayed as ”Ambient Pressure” in the HMI. | PC 2.x, PC 3.x |
| 40230 | Boost Pressure | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: psi Lower Limit: Upper Limit: | Monitor point for the Boost Absolute Pressure | PC 2.x, PC 3.x |
| 40231 | CAN Datalink Status | Read Only | 0: Inactive 1: Active 2: Failed | Indicates the status of the CAN datalink | PC 2.x, PC 3.x |
| 40232 | Crankcase Pressure | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: psi Lower Limit: -35.67 Upper Limit: 38 | Monitor point for the Crankcase Pressure. | PC 2.x, PC 3.x |
| 40235 | ECM Derate Request | Read Only | 0: No Derate Request 1: Derate Request 2: Error 3: Don’t Care | Request made by the ECS for a reduction in load | PC 2.x, PC 3.x |
| 40236 | Engine Application Type | Read Only | 0: ECM 1: Hydro-Mechanical | Monitor point for the output of the Engine application type. Either ECM (CAN) or Hydro- Mechanical. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40237 | Engine State | Read Only | 0: Stop 1: Ventilation 2: Start 3: Run 4: Normal Shutdown 5: Emergency Shutdown 6: Error 7: Don’t Care 8: Rapid Start 9: Reserved 10: Reserved 11: Reserved 12: Reserved 13: Reserved 14: Reserved 15: Don’t Care / Take No Action | ECS engine state indication | PC 2.x, PC 3.x |
| 40238 | PGI Major Version | Read Only | Multiplier :1 Offset: 0 Size (bits): 8 Sign: U Unit: NA Lower Limit: 0 Upper Limit: 225 Default: NA | Displays Power Generation Interface Major Version to which Engine Software is complying | PC 3.x |
| 40239 | PGI Minor Version | Read Only | Multiplier :1 Offset: 0 Size (bits): 8 Sign: U Unit: NA Lower Limit: 0 Upper Limit: 225 Default: NA | Displays Power Generation Interface Minor Version to which Engine Software is complying | PC 3.x |
| 40240 | PGI Informational Version | Read Only | Multiplier :1 Offset: 0 Size (bits): 8 Sign: U Unit: NA Lower Limit: 0 Upper Limit: 225 Default: NA | Displays Power Generation Interface Informational Version to which Engine Software is complying | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40242 | Aftercooler Temperature | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: -40 Upper Limit: 410 Default: NA | Monitor point for the Aftercooler Temperature. | PC 2.x, PC 3.x |
| 40243 | Internal ECM Module 1 Temperature | Read Only | Multiplier : 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: NA Upper Limit: NA Default: NA | Internal temperature of the engine electronic control module 1 | PC 3.x |
| 40244 | Internal ECM Module 2 Temperature | Read Only | Multiplier : 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: NA Upper Limit: NA Default: NA | Internal temperature of the engine electronic control module 2 | PC 3.x |
| 40245 | Internal ECM Module 3 Temperature | Read Only | Multiplier : 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: NA Upper Limit: NA Default: NA | Internal temperature of the engine electronic control module 3 | PC 3.x |
| 40246 | Internal ECM Module 4 Temperature | Read Only | Multiplier : 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: NA Upper Limit: NA Default: NA | Internal temperature of the engine electronic control module 4 | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40247 | ECM Module 1 Battery Voltage | Read Only | Multiplier : 0.1 Offset: 0 Size (bits): 16 Sign: U Units: Vdc Lower Limit: 0 Upper Limit: 65535 Default: NA | Engine Control Module 1 Battery Voltage. | PC 3.x |
| 40248 | ECM Module 2 Battery Voltage | Read Only | Multiplier : 0.1 Offset: 0 Size (bits): 16 Sign: U Units: Vdc Lower Limit: 0 Upper Limit: 65535 Default: NA | Engine Control Module 2 Battery Voltage. | PC 3.x |
| 40249 | ECM Module 3 Battery Voltage | Read Only | Multiplier : 0.1 Offset: 0 Size (bits): 16 Sign: U Units: Vdc Lower Limit: 0 Upper Limit: 65535 Default: NA | Engine Control Module 3 Battery Voltage. | PC 3.x |
| 40250 | ECM Module 4 Battery Voltage | Read Only | Multiplier : 0.1 Offset: 0 Size (bits): 16 Sign: U Units: Vdc Lower Limit: 0 Upper Limit: 65535 Default: NA | Engine Control Module 4 Battery Voltage. | PC 3.x |
| 40254 | Fuel Supply Pressure | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: psi Lower Limit: 0 Upper Limit: 145 | Monitor point for the Fuel Supply Pressure. Displayed as ”Fuel Supply Pressure” in the HMI. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40257 | Intake Manifold 4 Temperature | Read Only | Multiplier : 0.1 Offset: 0 Size (bits): 16 Sign: S Units: degF Lower Limit: -40 Upper Limit: 410 Default: NA | Monitor point for the Intake Manifold 4 Temperature | PC 2.x, PC 3.x |
| 40258 | Fuel Outlet Pressure | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 32 Sign: U Unit: psi Lower Limit: 0 Upper Limit: 36404 | Monitor point for the Fuel Outlet Pressure. Displayed as ”Fuel Rail Pressure” in the HMI. | PC 2.x, PC 3.x |
| 40259 | Fuel Outlet Pressure | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 32 Sign: U Unit: psi Lower Limit: 0 Upper Limit: 36404 | Monitor point for the Fuel Outlet Pressure. Displayed as ”Fuel Rail Pressure” in the HMI. | PC 2.x, PC 3.x |
| 40260 | Intake Manifold 2 Temperature | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: -40 Upper Limit: 410 | Monitor point for the Intake Manifold 2 Temperature | PC 2.x, PC 3.x |
| 40261 | Intake Manifold 3 Temperature | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: -40 Upper Limit: 410 | Monitor point for the Intake Manifold 3 Temperature | PC 2.x, PC 3.x |
| 40264 | Percent Engine Torque/Duty Cycle | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: % Lower Limit: -40 Upper Limit: 410 | Monitor point for the percent engine torque output and the governor percent duty cycle output when used with the HM ECM | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40276 | Post-Filter Oil Pressure | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: psi Lower Limit: 0 Upper Limit: 145 | Monitor point for the Post- Filter Oil Pressure | PC 2.x, PC 3.x |
| 40277 | Pre-Filter Oil Pressure | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: psi Lower Limit: 0 Upper Limit: 145 | Monitor point for the Pre-Filter Oil Pressure | PC 2.x, PC 3.x |
| 40278 | Configurable Input #14 Switch | Read Only | 0: Inactive 1: Active | Configurable Input #14 input software state status. Gives software Inactive/Active state | PC 2.x, PC 3.x |
| 40279 | Turbocharger 1 Speed | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: RPM Lower Limit: 0 Upper Limit: 257000 | Monitor point for the Turbocharger 1 Speed | PC 2.x, PC 3.x |
| 40280 | Turbocharger 1 Speed | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: RPM Lower Limit: 0 Upper Limit: 257000 | Monitor point for the Turbocharger 1 Speed | PC 2.x, PC 3.x |
| 40281 | Turbocharger 2 Boost Pressure | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 32 Sign: U Unit: psi Lower Limit: Upper Limit: | Monitor point for the Turbocharger 2 Boost Pressure | PC 2.x, PC 3.x |
| 40282 | Water in Fuel Indicator | Read Only | 0: No 1: Yes | Water in Fuel Indication | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40283 | Controller Mode | Read Only | 0: Off 1: Ready 2: Setup 3: Starting 4: Idle 5: Rated 6: Stop Normal 7: Stop Emergency 8: Factory Test 9: Wait to Power Down | The controller mode | PC 2.x, PC 3.x |
| 40285 | Power Down Mode Timer | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 0 Upper Limit: 600 | Timer to count down the time before the control goes to sleep | PC 2.x, PC 3.x |
| 40286 | Setup Mode Timer | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: NA Upper Limit: NA Default: NA | Time spent in Setup Mode. | PC 2.x PC3.x |
| 40287 | Tool Wake-up Command | Read only | 0: Inactive 1: Active | The control output to the common wake-up line to wake up other devices | PC 2.x PC 3.x |
| 40289 | Active Schedule | Read only | 0: None 1: Program 1 2: Program 2 3: Program 3 4: Program 4 5: Program 5 6: Program 6 7: Program 7 8: Program 8 9: Program 9 10: Program 10 11: Program 11 12: Program 12 13: Exception 1 14: Exception 2 | Indicates the currently active scheduler program or exception. | PC 2.x PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40290 | Controller On Time | Read Only | Multiplier : 1 Offset: 0 Size (bits): 32 Sign: U Unit: seconds Lower Limit: 0 Upper Limit: 4294967295 Default: NA | Controller ON time in seconds. Upper limit is 136 years. | PC 2.x PC 3.x |
| 40291 | Controller On Time | Read Only | Multiplier : 1 Offset: 0 Size (bits): 32 Sign: U Unit: seconds Lower Limit: 0 Upper Limit: 4294967295 Default: NA | Controller ON time in seconds. Upper limit is 136 years. | PC 2.x PC 3.x |
| 40298 | Runs Since Reset | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: Lower Limit: 0 Upper Limit: 4294967290 | Number of runs since the last reset. Upper limit is 2^32 -1. | PC 2.x, PC 3.x |
| 40299 | Runs Since Reset | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: Lower Limit: 0 Upper Limit: 4294967290 | Number of runs since the last reset. Upper limit is 2^32 -1. | PC 2.x, PC 3.x |
| 40300 | Remote Start Switch(Modb us) | Read/Write | 0: Inactive 1: Active | Modbus Remote Start | PC 2.x, PC 3.x |
| 40301 | Fault Reset (Modbus) | Read/Write | 0: Inactive 1: Active | Modbus fault reset. | PC 2.x, PC 3.x |
| 40320 | Start Inhibit No1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the operator panel when this fault becomes active | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40321 | Start Inhibit No1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the operator panel when this fault becomes active | PC 3.x |
| 40322 | Start Inhibit No1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the operator panel when this fault becomes active | PC 3.x |
| 40323 | Start Inhibit No1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the operator panel when this fault becomes active | PC 3.x |
| 40324 | Start Inhibit No1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the operator panel when this fault becomes active | PC 3.x |
| 40325 | Start Inhibit No1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the operator panel when this fault becomes active | PC 3.x |
| 40326 | Start Inhibit No1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the operator panel when this fault becomes active | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40327 | Start Inhibit No1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the operator panel when this fault becomes active | PC 3.x |
| 40328 | Start Inhibit No1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the operator panel when this fault becomes active | PC 3.x |
| 40329 | Start Inhibit No1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the operator panel when this fault becomes active | PC 3.x |
| 40330 | Start Inhibit No1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the operator panel when this fault becomes active | PC 3.x |
| 40331 | Start Inhibit No1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the operator panel when this fault becomes active | PC 3.x |
| 40332 | Start Inhibit No1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the operator panel when this fault becomes active | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40333 | Start Inhibit No1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the operator panel when this fault becomes active | PC 3.x |
| 40334 | Start Inhibit No1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the operator panel when this fault becomes active | PC 3.x |
| 40335 | Start Inhibit No1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the operator panel when this fault becomes active | PC 3.x |
| 40336 | Start Inhibit No1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the operator panel when this fault becomes active | PC 3.x |
| 40337 | Start Inhibit No1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the operator panel when this fault becomes active | PC 3.x |
| 40338 | Start Inhibit No1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the operator panel when this fault becomes active | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40339 | Start Inhibit No1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the operator panel when this fault becomes active | PC 3.x |
| 40340 | Start Inhibit No2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the operator panel when this fault becomes active. | PC 3.x |
| 40341 | Start Inhibit No2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the operator panel when this fault becomes active. | PC 3.x |
| 40342 | Start Inhibit No2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the operator panel when this fault becomes active. | PC 3.x |
| 40343 | Start Inhibit No2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the operator panel when this fault becomes active. | PC 3.x |
| 40344 | Start Inhibit No2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the operator panel when this fault becomes active. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40345 | Start Inhibit No2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the operator panel when this fault becomes active. | PC 3.x |
| 40346 | Start Inhibit No2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the operator panel when this fault becomes active. | PC 3.x |
| 40347 | Start Inhibit No2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the operator panel when this fault becomes active. | PC 3.x |
| 40348 | Start Inhibit No2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the operator panel when this fault becomes active. | PC 3.x |
| 40349 | Start Inhibit No2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the operator panel when this fault becomes active. | PC 3.x |
| 40350 | Start Inhibit No2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the operator panel when this fault becomes active. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40351 | Start Inhibit No2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the operator panel when this fault becomes active. | PC 3.x |
| 40352 | Start Inhibit No2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the operator panel when this fault becomes active. | PC 3.x |
| 40353 | Start Inhibit No2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the operator panel when this fault becomes active. | PC 3.x |
| 40354 | Start Inhibit No2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the operator panel when this fault becomes active. | PC 3.x |
| 40355 | Start Inhibit No2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the Operator panel when this fault becomes active. | PC 3.x |
| 40356 | Start Inhibit No2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the Operator panel when this fault becomes active. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40357 | Start Inhibit No2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the Operator panel when this fault becomes active. | PC 3.x |
| 40358 | Start Inhibit No2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the Operator panel when this fault becomes active. | PC 3.x |
| 40359 | Start Inhibit No2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the Operator panel when this fault becomes active. | PC 3.x |
| 40360 | Start Inhibit No3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the Operator panel when this fault becomes active. | PC 3.x |
| 40361 | Start Inhibit No3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the Operator panel when this fault becomes active. | PC 3.x |
| 40362 | Start Inhibit No3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the Operator panel when this fault becomes active. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40363 | Start Inhibit No3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the Operator panel when this fault becomes active. | PC 3.x |
| 40364 | Start Inhibit No3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the Operator panel when this fault becomes active. | PC 3.x |
| 40365 | Start Inhibit No3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the Operator panel when this fault becomes active. | PC 3.x |
| 40366 | Start Inhibit No3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the Operator panel when this fault becomes active. | PC 3.x |
| 40367 | Start Inhibit No3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the Operator panel when this fault becomes active. | PC 3.x |
| 40368 | Start Inhibit No3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the Operator panel when this fault becomes active. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40369 | Start Inhibit No3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the Operator panel when this fault becomes active. | PC 3.x |
| 40370 | Start Inhibit No3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the Operator panel when this fault becomes active. | PC 3.x |
| 40371 | Start Inhibit No3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the Operator panel when this fault becomes active. | PC 3.x |
| 40372 | Start Inhibit No3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the Operator panel when this fault becomes active. | PC 3.x |
| 40373 | Start Inhibit No3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the Operator panel when this fault becomes active. | PC 3.x |
| 40374 | Start Inhibit No3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the Operator panel when this fault becomes active. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40375 | Start Inhibit No3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the Operator panel when this fault becomes active. | PC 3.x |
| 40376 | Start Inhibit No3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the Operator panel when this fault becomes active. | PC 3.x |
| 40377 | Start Inhibit No3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the Operator panel when this fault becomes active. | PC 3.x |
| 40378 | Start Inhibit No3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the Operator panel when this fault becomes active. | PC 3.x |
| 40379 | Start Inhibit No3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 20 character string for use by the Operator panel when this fault becomes active. | PC 3.x |
| 40422 | Fault Status Bitmap 23 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65530 Default: NA | 16 bit fault bitmap for Modbus interface. | PC 2.x PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40423 | Fault Status Bitmap 24 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65530 Default: NA | 16 bit fault bitmap for Modbus interface. | PC 2.x PC 3.x |
| 40424 | Fault Status Bitmap 25 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65530 Default: NA | 16 bit fault bitmap for Modbus interface. | PC 2.x PC3.x |
| 40425 | Event Status Bitmap 2 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit fault bitmap for Modbus interface. | PC 2.x PC 3.x |
| 40426 | Event Status Bitmap 3 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit fault bitmap for Modbus interface. | PC 2.x PC 3.x |
| 40427 | Fault Status Bitmap 26 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit fault bitmap for Modbus interface. | PC 2.x PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40428 | Fault Status Bitmap 32 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit event bitmap for Modbus interface and Tier4F 16 bit Diesel Fault Bitmap for Modbus interface | PC 3.x |
| 40430 | Event Status Bitmap 1 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit fault bitmap for Modbus interface. | PC 2.x PC 3.x |
| 40431 | Fault Status Gas Bitmap 1 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40432 | Fault Status Gas Bitmap 2 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40433 | Fault Status Gas Bitmap 3 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40434 | Fault Status Gas Bitmap 4 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40435 | Fault Status Gas Bitmap 5 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40436 | Fault Status Gas Bitmap 6 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40437 | Fault Status Gas Bitmap 7 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40438 | Fault Status Gas Bitmap 8 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40439 | Fault Status Gas Bitmap 9 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40440 | Fault Status Gas Bitmap 10 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40441 | Fault Status Gas Bitmap 11 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40442 | Fault Status Gas Bitmap 12 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40443 | Fault Status Gas Bitmap 13 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40444 | Fault Status Gas Bitmap 14 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40445 | Fault Status Gas Bitmap 15 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40446 | Fault Status Gas Bitmap 16 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40447 | Fault Status Gas Bitmap 17 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40448 | Fault Status Gas Bitmap 18 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40449 | Fault Status Gas Bitmap 19 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40450 | Fault Status Gas Bitmap 20 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40451 | Fault Status Gas Bitmap 21 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40452 | Fault Status Gas Bitmap 22 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40453 | Fault Status Gas Bitmap 23 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40454 | Fault Status Gas Bitmap 24 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40455 | Fault Status Gas Bitmap 25 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40456 | Fault Status Gas Bitmap 26 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40457 | Fault Status Gas Bitmap 27 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40458 | Fault Status Gas Bitmap 28 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40459 | Fault Status Gas Bitmap 29 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40460 | Fault Status Gas Bitmap 30 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40461 | Fault Status Gas Bitmap 31 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40462 | Fault Status Gas Bitmap 32 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40463 | Fault Status Gas Bitmap 33 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40464 | Fault Status Gas Bitmap 34 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40465 | Fault Status Gas Bitmap 35 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40466 | Fault Status Gas Bitmap 36 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40467 | Fault Status Gas Bitmap 37 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40468 | Fault Status Gas Bitmap 38 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40469 | Fault Status Gas Bitmap 39 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65530 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40470 | Fault Status Gas Bitmap 40 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40471 | Fault Status Gas Bitmap 41 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40472 | Fault Status Gas Bitmap 42 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40473 | Fault Status Gas Bitmap 43 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40474 | Fault Status Gas Bitmap 44 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40475 | Fault Status Gas Bitmap 45 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40476 | Fault Status Gas Bitmap 46 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40477 | Fault Status Gas Bitmap 47 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40478 | Fault Status Gas Bitmap 48 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40479 | Fault Status Gas Bitmap 49 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40480 | Fault Status Gas Bitmap 50 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40481 | Fault Status Gas Bitmap 51 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40482 | Fault Status Gas Bitmap 52 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40483 | Fault Status Gas Bitmap 53 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40484 | Fault Status Gas Bitmap 54 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40485 | Fault Status Gas Bitmap 55 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40486 | Fault Status Gas Bitmap 56 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40487 | Fault Status Gas Bitmap 57 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40488 | Fault Status Gas Bitmap 58 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40489 | Fault Status Gas Bitmap 59 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40490 | Fault Status Gas Bitmap 60 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40491 | Fault Status Gas Bitmap 61 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40492 | Fault Status Gas Bitmap 62 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40493 | Fault Status Gas Bitmap 63 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40494 | Fault Status Gas Bitmap 64 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit Gas fault bitmap for Modbus interface. | PC 3.x |
| 40495 | AT Fault Status Bitmap 1 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65535 Default: NA | 16 bit AT Fault Bitmap for Modbus interface | PC 3.x |
| 40496 | Fault Status Bitmap 27 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65530 Default: NA | 16 bit fault bitmap for Modbus interface | PC 3.x |
| 40497 | Fault Status Bitmap 28 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65530 Default: NA | 16 bit fault bitmap for Modbus interface | PC 3.x |
| 40498 | Fault Status Bitmap 29 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65530 Default: NA | 16 bit fault bitmap for Modbus interface | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40499 | Fault Status Bitmap 30 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65530 Default: NA | 16 bit fault bitmap for Modbus interface | PC 3.x |
| 40500 | Low Fuel Switch | Read Only | 0: Inactive 1: Active | Low Fuel input software state status. Gives software Inactive/Active state | PC 2.x, PC 3.x |
| 40501 | Low Fuel/Configur able Input #6 Switch | Read Only | 0: Inactive 1: Active | This is the status of the Configurable Input #6. | PC 2.x, PC 3.x |
| 40503 | Differential Fault Trip | Read Only | 0: Inactive 1: Active 2: Reserved 3: Not Available | Differential fault trip monitor point | PC 3.x |
| 40504 | Master First Start Input A | Read Only | 0: Inactive 1: Active | This is the status of the Master First Start A input | PC 3.x |
| 40505 | Fire Trip | Read Only | 0: Inactive 1: Active | Fire trip monitor point. | PC 3.x |
| 40506 | Master First Start Input B Switch | Read Only | 0: Inactive 1: Active | Master First Start Input B input software state status. Gives software Inactive/Active state. | PC 3.x |
| 40507 | Masterless Load Demand Enable Switch | Read Only | 0: Inactive 1: Active | Masterless Load Demand Enable Switch function output status. Gives software Inactive/Active state | PC 3.x |
| 40508 | Predictive Load Enable Switch | Read Only | 0: Inactive 1: Active | Predictive Load Enable Switch function output status. Gives software Inactive/Active state | PC 3.x |
| 40509 | PTC Mode Switch | Read Only | 0: Inactive 1: Active | PTC Mode Switch function output status. Gives software Inactive/Active state | PC 3.x |
| 40510 | Extended Parallel/Confi gurable Input #32 Switch | Read Only | 0: Inactive 1: Active | This is the status of the Configurable Input #32. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40511 | Ramp Load/Unload Switch | Read Only | 0: Load 1: Unload | Ramp Load/Unload input software state status | PC 3.x |
| 40512 | Remote E- stop Switch | Read Only | 0: Inactive 1: Active | Remote E–stop input software state status. Gives software Inactive/Active state | PC 2.x, PC 3.x |
| 40513 | Remote Start Switch | Read Only | 0: Inactive 1: Active | Remote Start input software state status. Gives software Inactive/Active state | PC 2.x, PC 3.x |
| 40514 | Retransfer Inhibit Switch | Read Only | 0: Inactive 1: Active | Retransfer Inhibit input software state status. Gives software Inactive/Active state | PC 3.x |
| 40515 | Retransfer Inhibit/Config urable Input #21 Switch | Read Only | 0: Inactive 1: Active | This is the status of the Configurable Input #21. | PC 3.x |
| 40516 | Rupture Basin Switch | Read Only | 0: Inactive 1: Active | Rupture Basin input software state status. Gives software Inactive/Active state | PC 2.x, PC 3.x |
| 40517 | Rupture Basin/Configu rable Input #12 Switch | Read Only | 0: Inactive 1: Active | This is the status of the Configurable Input #12. | PC 2.x, PC 3.x |
| 40518 | Speed Droop Enable Switch | Read Only | 0: Inactive 1: Active | Monitors the Speed Droop Enable Switch function; Inactive or Active state | PC 2.x, PC 3.x |
| 40519 | Start Type Switch | Read Only | 0: Inactive 1: Active | Start Type input software state status. Gives software Inactive/Active state | PC 2.x, PC 3.x |
| 40520 | Sync Enable Switch | Read Only | 0: Inactive 1: Active | Sync Enable input software state status. Gives software Inactive/Active state | PC 3.x |
| 40521 | Sync Enable/Confi gurable Input #30 Switch | Read Only | 0: Inactive 1: Active | This is the status of the Configurable Input #30. | PC 3.x |
| 40522 | Tool Wakeup Switch | Read Only | 0: Inactive 1: Active | Tool Wake-up input software state status. Gives software Inactive/Active state | PC 2.x, PC 3.x |
| 40523 | Transfer Inhibit Switch | Read Only | 0: Inactive 1: Active | Transfer Inhibit input software state status. Gives software Inactive/Active state | PC 3.x |
| 40524 | Transfer Inhibit/Config urable Input #20 Switch | Read Only | 0: Inactive 1: Active | This is the status of the Configurable Input #20. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40525 | Utility CB Inhibit/Config urable Input #25 Switch | Read Only | 0: Inactive 1: Active | This is the status of the Configurable Input #25. | PC 3.x |
| 40526 | Utility CB Pos B/Configurabl e Input #23 Switch | Read Only | 0: Inactive 1: Active | This is the status of the Configurable Input #23. | PC 3.x |
| 40527 | Utility CB Tripped/Confi gurable Input #24 Switch | Read Only | 0: Inactive 1: Active | This is the status of the Configurable Input #24. | PC 3.x |
| 40528 | Utility Single Mode Verify/Config urable Input #29 Switch | Read Only | 0: Inactive 1: Active | This is the status of the Configurable Input #29. | PC 3.x |
| 40529 | Utility CB Inhibit Switch | Read Only | 0: Inactive 1: Active | Utility CB Inhibit input software state status. Gives software Inactive/Active state | PC 3.x |
| 40530 | Utility CB Pos A Switch | Read Only | 0: Inactive 1: Active | Utility CB Pos A input software state status. Gives software Inactive/Active state | PC 3.x |
| 40531 | Utility CB Pos B Switch | Read Only | 0: Inactive 1: Active | Utility CB Pos B input software state status. Gives software Inactive/Active state | PC 3.x |
| 40532 | Utility CB Tripped Switch | Read Only | 0: Inactive 1: Active | Utility CB Tripped input software state status. Gives software Inactive/Active state | PC 3.x |
| 40533 | Utility Single Mode Verify Switch | Read Only | 0: Inactive 1: Active | Utility Single Mode Verify input software state status. Gives software Inactive/Active state | PC 3.x |
| 40534 | Voltage Droop Enable Switch | Read Only | 0: Inactive 1: Active | Voltage Droop Enable Switch function output status. Gives software Inactive/Active state. | PC 2.x, PC 3.x |
| 40535 | Configurable Output #1 Status | Read Only | 0: Inactive 1: Active | Indicates if the output’s status is Inactive or Active | PC 2.x, PC 3.x |
| 40536 | Configurable Output #2 Status | Read Only | 0: Inactive 1: Active | Indicates if the output’s status is Inactive or Active | PC 2.x, PC 3.x |
| 40537 | Configurable Output #20 Status | Read Only | 0: Inactive 1: Active | Indicates if the output’s status is Inactive or Active | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40538 | Configurable Output #21 Status | Read Only | 0: Inactive 1: Active | Indicates if the output’s status is Inactive or Active | PC 3.x |
| 40539 | Configurable Output #22 Status | Read Only | 0: Inactive 1: Active | Indicates if the output’s status is Inactive or Active | PC 3.x |
| 40540 | Configurable Output #3 Status | Read Only | 0: Inactive 1: Active | Indicates if the output’s status is Inactive or Active | PC 2.x, PC 3.x |
| 40541 | Configurable Output #4 Status | Read Only | 0: Inactive 1: Active | Indicates if the output’s status is Inactive or Active | PC 2.x, PC 3.x |
| 40542 | Delayed Off / Configurable Output #10 Status | Read Only | 0: Inactive 1: Active | Indicates if the output’s status is Inactive or Active | PC 2.x, PC 3.x |
| 40543 | Fuel Shutoff Status | Read Only | 0: Inactive 1: Active | Indicates if the output’s status is Inactive or Active | PC 2.x, PC 3.x |
| 40545 | Genset CB Open Status | Read Only | 0: Inactive 1: Active | Indicates if the output’s status is Inactive or Active | PC 3.x |
| 40546 | Hold Power On Driver Status | Read Only | 0: Inactive 1: Active | Indicates if the output’s status is Inactive or Active | PC 2.x, PC 3.x |
| 40547 | Keyswitch Status | Read Only | 0: Inactive 1: Active | Indicates if the output’s status is Inactive or Active | PC 2.x, PC 3.x |
| 40548 | KW/kVAR Load Share Relay Status | Read Only | 0: Inactive 1: Active | Indicates if the output’s status is Inactive or Active | PC 3.x |
| 40549 | Load Dump / Configurable Output #11 Status | Read Only | 0: Inactive 1: Active | Indicates if the output’s status is Inactive or Active | PC 2.x, PC 3.x |
| 40550 | Local Status / Configurable Output #7 Status | Read Only | 0: Inactive 1: Active | Indicates if the output’s status is Inactive or Active | PC 2.x, PC 3.x |
| 40551 | Master First Start Output Status | Read Only | 0: Inactive 1: Active | Indicates if the output’s status is Inactive or Active | PC 3.x |
| 40552 | Oil Priming Pump / Configurable Output #6 Status | Read Only | 0: Inactive 1: Active | Indicates if the output’s status is Inactive or Active | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40553 | Ready To Load /Configurable Output #5 Status | Read Only | 0: Inactive 1: Active | Indicates if the output’s status is Inactive or Active | PC 2.x, PC 3.x |
| 40554 | Run Relay #1 Status | Read Only | 0: Inactive 1: Active | Indicates if the output’s status is Inactive or Active | PC 2.x, PC 3.x |
| 40555 | Run Relay #2 Status | Read Only | 0: Inactive 1: Active | Indicates if the output’s status is Inactive or Active | PC 2.x, PC 3.x |
| 40556 | Speed/Voltag e Bias Relay Status | Read Only | 0: Inactive 1: Active | Indicates if the output’s status is Inactive or Active | PC 3.x |
| 40557 | Starter Status | Read Only | 0: Inactive 1: Active | Indicates if the output’s status is Inactive or Active | PC 2.x, PC 3.x |
| 40558 | Tool Wake-up Driver Status | Read Only | 0: Inactive 1: Active | Indicates if the output’s status is Inactive or Active | PC 2.x, PC 3.x |
| 40559 | Utility CB Close Status | Read Only | 0: Inactive 1: Active | Indicates if the output’s status is Inactive or Active | PC 3.x |
| 40560 | Utility CB Open Status | Read Only | 0: Inactive 1: Active | Indicates if the output’s status is Inactive or Active | PC 3.x |
| 40561 | Common Alarm Fault Status | Read Only | 0: Inactive 1: Active | The status of the Common Alarm Fault | PC 2.x, PC 3.x |
| 40562 | Common Shutdown Command | Read Only | 0: Inactive 1: Active | The status of the common shutdown command | PC 2.x, PC 3.x |
| 40563 | Common Shutdown Event Status | Read Only | 0: Inactive 1: Active | The status of the Common Shutdown Event | PC 2.x, PC 3.x |
| 40564 | Common Shutdown w/Cooldown Command | Read Only | 0: Inactive 1: Active | The status of the common shutdown w/Cooldown command | PC 3.x |
| 40565 | Common Warning Event Status | Read Only | 0: Inactive 1: Active | The status of the Common Warning Event | PC 2.x, PC 3.x |
| 40566 | Delayed Shutdown Flag | Read Only | 0: Inactive 1: Active | Monitor point for the Delayed shutdown flag. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40567 | Delayed Shutdown Timer | Read Only | Multiplier : 0.1 Offset: 0 Size (bits): 16 Sign: U Units: Seconds Lower Limit: 0 Upper Limit: 3 Default: NA | Monitor point for the Delayed shutdown timer. | PC 2.x, PC 3.x |
| 40568 | Derate Request | Read Only | Multiplier : 1 Offset: 0 Size (bits): 8 Sign: U Units: % Lower Limit: 0 Upper Limit: 100 Default: NA | The requested % derate from the derate request logic. | PC 2.x PC 3.x |
| 40569 | Fault Detection Reset | Read Only | 0: Inactive 1: Active | The status of the Fault Detection Reset logic. | PC 2.x, PC 3.x |
| 40570 | Fault Reset Command | Read Only | 0: Inactive 1: Active | One shot due to fault reset switch being active. | PC 2.x, PC 3.x |
| 40571 | Remote Shutdown Fault Reset Signal | Read Only | 0: Inactive 1: Active | Becomes active when a remote fault reset signal has been initiated. | PC 2.x, PC 3.x |
| 40572 | Shutdown Fault Reset | Read Only | 0: Inactive 1: Active | The status of the Shutdown Fault reset logic. | PC 2.x, PC 3.x |
| 40573 | Battle Short Flag | Read Only | 0: Inactive 1: Active | Monitor point indicating the enabled/disabled status of the battle short function | PC 2.x, PC 3.x |
| 40574 | Auto Command | Read Only | 0: Not Auto 1: Auto | The output of the Auto Command OR logic | PC 2.x, PC 3.x |
| 40575 | Auto Command Inputs | Read Only | Multiplier : 1 Offset: 0 Size (bits): 8 Sign: U Units: NA Lower Limit: NA Upper Limit: NA Default: NA | Bitmask to show the inputs to the Command output which are currently on | PC 2.x, PC 3.x |
| 40576 | AVR Regulation Mode | Read Only | 0: Voltage 1: Current | The operational mode of the AVR as a voltage or a current regulator | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40577 | Base Frequency | Read Only | Multiplier: 0.001 Offset: 0 Size (bits): 32 Sign: U Unit: Hz Lower Limit: Upper Limit: | Provides a point to monitor the base frequency | PC 2.x, PC 3.x |
| 40578 | Base Frequency | Read Only | Multiplier: 0.001 Offset: 0 Size (bits): 32 Sign: U Unit: Hz Lower Limit: Upper Limit: | Provides a point to monitor the base frequency | PC 2.x, PC 3.x |
| 40579 | Battery Charging Fault Integrator | Read Only | Multiplier : 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Hz Lower Limit: 0 Upper Limit: 300 Default: NA | Time spent while the charger is sensed as failed | PC 2.x, PC 3.x |
| 40580 | Control Switch Position | Read Only | 0: Off 1: Manual 2: Auto | Current position of the generator set switch panel Off-Run-Auto switch as seen by the generator set control. SEE ALSO ADDRESS 40010. NOTE: Both address 40580 and 40010 show the same information however the specification for each is different. | PC 2.x, PC 3.x |
| 40581 | Controlled Shutdown Status | Read /Write | 0: Inactive 1: Pending 2: Shutdown | Indicates status of the controlled shutdown logic | PC 3.x |
| 40582 | Crank Allowed | Read Only | 0: False 1: True | Monitor Point indicates if Cranking is Allowed by the Prelube State Machin | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40583 | Dead Battery Prevention Counter | Read Only | Multiplier : 1 Offset: 0 Size (bits): 8 Sign: U Units: NA Lower Limit: 0 Upper Limit: 250 Default: NA | Tracks the number of crank attempts in order to limit the attempts when the battery is so low that the control resets | PC 2.x, PC 3.x |
| 40584 | Delayed Off Command | Read Only | 0: Inactive 1: Active 2: Reserved 3: Not Available | The status of the delayed run command off logic. | PC 2.x, PC 3.x |
| 40586 | Excitation State | Read Only | 0: Disabled 1: Enabled | Shows the enable status of the excitation enabled = regulator on. | PC 2.x, PC 3.x |
| 40587 | Exercise Command | Read Only | 0: Inactive 1: Active 2: Reserved 3: Not Available | The output of the Exercise Command OR logic | PC 2.x, PC 3.x |
| 40588 | Exercise Command Inputs | Read Only | Multiplier : 1 Offset: 0 Size (bits): 8 Sign: U Units: NA Lower Limit: 0 Upper Limit: 250 Default: NA | Bitmask to show the inputs to the Command output which are currently on | PC 2.x, PC 3.x |
| 40589 | Exercise Time Remaining | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: hours Lower Limit: 0 Upper Limit: 25 | Time remaining until exercise stop sequence begins | PC 2.x, PC 3.x |
| 40590 | Extended Parallel Switch Command | Read Only | 0: Stop 1: Start | The output of the Extended Parallel Switch Command OR logic | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40591 | Extended Parallel Switch Command Inputs | Read Only | Multiplier : 1 Offset: 0 Size (bits): 8 Sign: U Units: NA Lower Limit: NA Upper Limit: NA Default: NA | Bitmask to show the inputs to the Command output which are currently on | PC 3.x |
| 40592 | Battle Short Command | Read Only | 0: Inactive 1: Active | Indicates status of battle short inputs | PC 2.x, PC 3.x |
| 40593 | Shutdown Fault Override | Read Only | 0: Inactive 1: Active | Indicates whether or not the genset will ignore non-critical shutdown faults | PC 2.x, PC 3.x |
| 40595 | Final Frequency Reference | Read Only | Multiplier: 0.001 Offset: 0 Size (bits): 32 Sign: U Unit: Hz Lower Limit: 0 Upper Limit: 100 | The frequency scaled version of the final speed reference | PC 2.x, PC 3.x |
| 40596 | Final Frequency Reference | Read Only | Multiplier: 0.001 Offset: 0 Size (bits): 32 Sign: U Unit: Hz Lower Limit: 0 Upper Limit: 100 | The frequency scaled version of the final speed reference | PC 2.x, PC 3.x |
| 40598 | Fuel Shutoff Command | Read Only | 0: Inactive 1: Active 2: Reserved 3: Not Available | The result of the FSO driver output command logic | PC 2.x, PC 3.x |
| 40599 | Genset Run Command | Read Only | 0: Emergency Stop 1: Stop 2: Load Demand Stop 3: Run | Genset run / stop states | PC 2.x, PC 3.x |
| 40600 | Configurable Input #1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40601 | Configurable Input #1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40602 | Configurable Input #1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40603 | Configurable Input #1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40604 | Configurable Input #1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40605 | Configurable Input #1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40606 | Configurable Input #1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40607 | Configurable Input #1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40608 | Configurable Input #1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40609 | Configurable Input #1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40610 | Configurable Input #1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40611 | Configurable Input #1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40612 | Configurable Input #1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40613 | Configurable Input #1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40614 | Configurable Input #1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40615 | Configurable Input #1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40620 | Configurable Input #2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40621 | Configurable Input #2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40622 | Configurable Input #2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40623 | Configurable Input #2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40624 | Configurable Input #2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40625 | Configurable Input #2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40626 | Configurable Input #2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40627 | Configurable Input #2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40628 | Configurable Input #2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40629 | Configurable Input #2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40630 | Configurable Input #2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40631 | Configurable Input #2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40632 | Configurable Input #2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40633 | Configurable Input #2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40634 | Configurable Input #2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40635 | Configurable Input #2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40640 | Configurable Input #13 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40641 | Configurable Input #13 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40642 | Configurable Input #13 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40643 | Configurable Input #13 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40644 | Configurable Input #13 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40645 | Configurable Input #13 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40646 | Configurable Input #13 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40647 | Configurable Input #13 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40648 | Configurable Input #13 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40649 | Configurable Input #13 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40650 | Configurable Input #13 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40651 | Configurable Input #13 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40652 | Configurable Input #13 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40653 | Configurable Input #13 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40654 | Configurable Input #13 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40655 | Configurable Input #13 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40660 | Configurable Input #14 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40661 | Configurable Input #14 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40662 | Configurable Input #14 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40663 | Configurable Input #14 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40664 | Configurable Input #14 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40665 | Configurable Input #14 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40666 | Configurable Input #14 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40667 | Configurable Input #14 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40668 | Configurable Input #14 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40669 | Configurable Input #14 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40670 | Configurable Input #14 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40671 | Configurable Input #14 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40672 | Configurable Input #14 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40673 | Configurable Input #14 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40674 | Configurable Input #14 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40675 | Configurable Input #14 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Trim to define the 16 character string for use by the Operator panel when this fault becomes active. | PC 2.x, PC 3.x |
| 40709 | Device Type (Modlon) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 8 Sign: U Unit: Lower Limit: Upper Limit: | This Modbus register is created for Modlon register mapping. This parameter is not associated with any logical. | PC 3.x |
| 40710 | Control Switch Position (Modlon) | Read Only | 0: Off 1: Manual 2: Auto | This Modbus register is created for Modlon register mapping. | PC 3.x |
| 40711 | Genset Run Sequence State (Modlon) | Read Only | 0: Stop 1: Time Delay to Start 2: Warmup at Idle 3: Rated Freq and Voltage 4: Cooldown / Stop Delay 5: Cooldown at Idle 6: Rated to Idle Transition Delay | This Modbus register is created for Modlon register mapping. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40712 | Most Recent Fault or Warning (Modlon) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Fault Code Lower Limit: Upper Limit: | This Modbus register is created for Modlon register mapping. This Modbus register is not associated with any logical Address | PC 3.x |
| 40713 | Fault Type (Modlon) | Read Only | 0: None 1: Warning 2: Derate 3: Shutdown with cooldown 4: Shutdown | This Modbus register is created for Modlon register mapping. This Modbus register is not associated with any logical address. | PC 3.x |
| 40714 | Genset % Standby Total kW (Modlon) | Read Only | Multiplier: 0.5 Offset: 0 Size (bits): 16 Sign: U Unit: % Lower Limit: Upper Limit: | This Modbus register is created for Modlon register mapping. Monitors the total generator set standby KW percentage output. Modbus has different multiplier than PCCnet. For Modlon use only, use multiplier 0.5 % | PC 3.x |
| 40715 | Genset Total kW (Modlon GenStatus) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: kW Lower Limit: Upper Limit: | This Modbus register is created for Modlon register mapping. Generator set total kW. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40716 | NFPA 110 Logical Status (Modlon) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: Lower Limit: Upper Limit: | This Modbus register is created for Modlon register mapping. 32–bit number to represent the status of the NFPA 110 logical. See NFPA110 bitmap. (See Table 28 on page 488). | PC 3.x |
| 40717 | NFPA 110 Logical Status (Modlon) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: Lower Limit: Upper Limit: | This Modbus register is created for Modlon register mapping. 32-bit number to represent the status of the NFPA 110 logical. (See Table 28 on page 488). | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40718 | Genset Frequency OP (Modlon) | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Hz Lower Limit: Upper Limit: | This Modbus register is created for Modlon register mapping. Generator set Frequency OP. Modbus has different multiplier than PCCNet. For Modlon use only, Multiplier/Units = 0.1 Hz | PC 3.x |
| 40719 | Genset Total Power Factor (Modlon) | Read Only | Multiplier: 0.00005 Offset: 0 Size (bits): 16 Sign: S Unit: PF Lower Limit: Upper Limit: | This Modbus register is created for Modlon register mapping. Generator set total power factor (L1+L2+L3). Modbus and PCCNet has different multiplier value. For Modlon, use 0.00005 PF. | PC 3.x |
| 40720 | Genset Total kVA (Modlon) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: kVA Lower Limit: Upper Limit: | This Modbus register is created for Modlon register mapping. Generator set total kVA | PC 3.x |
| 40721 | Genset Total kW (Modlon GenACData) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: kW Lower Limit: Upper Limit: | This Modbus register is created for Modlon register mapping. Generator set total kW in Gen AC Data. | PC 3.x |
| 40722 | Genset Total kVAR (Modlon) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: kVAR Lower Limit: Upper Limit: | This Modbus register is created for Modlon register mapping. Generator set total kVAR | PC 3.x |
| 40723 | Genset L1L2 Voltage (Modlon) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit: | This Modbus register is created for Modlon register mapping. Generator set L1L2 voltage | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40724 | Genset L2L3 Voltage (Modlon) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit: | This Modbus register is created for Modlon register mapping. Generator set L2L3 voltage | PC 3.x |
| 40725 | Genset L3L1 Voltage (Modlon) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit: | This Modbus register is created for Modlon register mapping. Generator set L3L1 voltage | PC 3.x |
| 40726 | Genset L1N Voltage (Modlon) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit: | This Modbus register is created for Modlon register mapping. Generator set L1N voltage | PC 3.x |
| 40727 | Genset L2N Voltage (Modlon) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit: | This Modbus register is created for Modlon register mapping. Generator set L2N voltage | PC 3.x |
| 40728 | Genset L3N Voltage (Modlon) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit: | This Modbus register is created for Modlon register mapping. Generator set L3N voltage | PC 3.x |
| 40729 | Genset L1 Current (Modlon) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Amps Lower Limit: Upper Limit: | Monitors the generator set L1 current value. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40730 | Genset L2 Current (Modlon) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Amps Lower Limit: Upper Limit: | Generator set L2 current | PC 3.x |
| 40731 | Genset L3 Current (Modlon) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Amps Lower Limit: Upper Limit: | This Modbus register is created for Modlon register mapping. Generator set L3 current | PC 3.x |
| 40732 | Genset % Standby L1 Current (Modlon) | Read Only | Multiplier: 0.5 Offset: 0 Size (bits): 16 Sign: U Unit: % Lower Limit: Upper Limit: | This Modbus register is created for Modlon register mapping. Monitors the generator set standby L1 current percentage output. Modbus and PCCNet have different multiplier value. For Modlon use 0.5 % | PC 3.x |
| 40733 | Genset % Standby L2 Current (Modlon) | Read Only | Multiplier: 0.5 Offset: 0 Size (bits): 16 Sign: U Unit: % Lower Limit: Upper Limit: | This Modbus register is created for Modlon register mapping. Monitors the generator set standby L2 current percentage output. Modbus and PCCNet has different multiplier value. For Modlon, use 0.5 % | PC 3.x |
| 40734 | Genset % Standby L3 Current (Modlon) | Read Only | Multiplier: 0.5 Offset: 0 Size (bits): 16 Sign: U Unit: % Lower Limit: Upper Limit: | This Modbus register is created for Modlon register mapping. Monitors the generator set standby L3 current percentage output. Modbus and PCCNet has different multiplier value. For Modlon use 0.5 % | PC 3.x |
| 40735 | Battery Voltage (Modlon) | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: Vdc Lower Limit: Upper Limit: | This Modbus register is created for Modlon register mapping. Battery voltage value. Modbus and PCCNet has different multiplier value. For Modlon use 0.1volts | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40736 | Oil Pressure (Modlon) | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: kPa Lower Limit: Upper Limit: | This Modbus register is created for Modlon register mapping. Monitor point for the Oil Pressure. Modbus and PCCNet have different multiplier value. For Modlon, use 0.1 KPA | PC 3.x |
| 40737 | Oil Temperature (Modlon) | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degK Lower Limit: Upper Limit: | This Modbus register is created for Modlon register mapping. Monitor point for the Oil Temperature. Modbus and PCCNet has different multiplier value. For Modlon use 0.1 deg Kelvin | PC 3.x |
| 40738 | Coolant Temperature (Modlon) | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degK Lower Limit: Upper Limit: | This Modbus register is created for Modlon register mapping. Monitor point for the Coolant Temperature. Modbus and PCCNet has different multiplier value. For Modlon, use 0.1deg Kelvin. | PC 3.x |
| 40739 | Intake Manifold Temperature (Modlon) | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degK Lower Limit: -40 Upper Limit: 410 | This Modbus register is created for Modlon register mapping. To monitor Intake Manifold Temperature. Modbus and PCCNet has different multiplier value. For Modlon, use 0.1 deg Kelvin | PC 3.x |
| 40740 | Fuel Temperature (Modlon) | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degK Lower Limit: -40 Upper Limit: 410 | This Modbus register is created for Modlon register mapping. Monitor point for the Fuel Temperature. Modbus and PCCNet has different multiplier value. For Modlon, use 0.1 deg Kelvin. | PC 3.x |
| 40741 | Fuel Rate (Modlon) | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: U Unit: gal/hr Lower Limit: Upper Limit: | This Modbus register is created for Modlon register mapping. Monitor point for the Fuel Rate. Modbus and PCCNet has different multiplier value. For Modlon, use 0.01 gph | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40742 | Average Engine Speed (Modlon) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: RPM Lower Limit: Upper Limit: | This Modbus register is created for Modlon register mapping. Monitor point for the Average Engine Speed. Modbus and PCCNet have different multiplier value. For Modlon, use 1 RPM. | PC 3.x |
| 40743 | Total Number of Runs (Modlon) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: Lower Limit: 0 Upper Limit: 4294967295 | This Modbus register is created for Modlon register mapping. Total number of generator set runs. | PC 3.x |
| 40744 | Engine Running Time (Modlon) | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: Upper Limit: | This Modbus register is created for Modlon register mapping. Total engine run time. Modbus has different multiplier than PCCNet. For Modbus, use 0.1 sec | PC 3.x |
| 40745 | Engine Running Time (Modlon) | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: Upper Limit: | This Modbus register is created for Modlon register mapping. Total engine run time. Modbus has different multiplier than PCCNet. For Modbus, use 0.1 sec | PC 3.x |
| 40746 | Genset Total Net kWh (Modlon) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: S Unit: kWh Lower Limit: -2147483648 Upper Limit: 2147483643 | This Modbus register is created for Modlon register mapping. Generator set total net kWh accumulation | PC 3.x |
| 40747 | Genset Total Net kWh (Modlon) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: S Unit: kWh Lower Limit: -2147483648 Upper Limit: 2147483643 | This Modbus register is created for Modlon register mapping. Generator set total net kWh accumulation | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40748 | Total Fuel Consumption (Modlon) | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 32 Sign: U Unit: gallons Lower Limit: Upper Limit: | This Modbus register is created for Modlon register mapping. Total fuel consumption since start of engine. Modbus and PCCNet has different multiplier value. For Modlon, use 0.01 Gallons | PC 3.x |
| 40749 | Total Fuel Consumption (Modlon) | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 32 Sign: U Unit: gallons Lower Limit: Upper Limit: | This Modbus register is created for Modlon register mapping. Total fuel consumption since start of engine. Modbus and PCCNet has different multiplier value. For Modlon, use 0.01 Gallons | PC 3.x |
| 40750 | Utility/Genset Bus Frequency (Modlon) | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Hz Lower Limit: Upper Limit: | This Modbus register is created for Modlon register mapping. Utility line frequency or Generator set Bus Frequency depending on Paralleling Application. Modbus and PCCNet has different multiplier value. For Modlon, use 0.1 Hz. | PC 3.x |
| 40751 | Utility/Genset Bus L1L2 Voltage (Modlon) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit: | This Modbus register is created for Modlon register mapping. Utility L1L2 Voltage or Generator set Bus L1L2 voltage depending on paralleling application. | PC 3.x |
| 40752 | Utility/Genset Bus L2L3 Voltage (Modlon) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit: | This Modbus register is created for Modlon register mapping. Utility L2L3 voltage | PC 3.x |
| 40753 | Utility/Genset Bus L3L1 Voltage (Modlon) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit: | This Modbus register is created for Modlon register mapping. Utility L3L1 voltage or Generator set Bus L3L1 voltage depending on paralleling application. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40754 | Utility/Genset Bus L1N Voltage (Modlon) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit: | This Modbus register is created for Modlon register mapping. Utility L1N voltage or Generator set Bus L1N voltage depending on paralleling application. | PC 3.x |
| 40755 | Utility/Genset Bus L2N Voltage (Modlon) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit: | This Modbus register is created for Modlon register mapping. Utility L2N voltage or Generator set Bus L2N voltage depending on paralleling application. | PC 3.x |
| 40756 | Utility/Genset Bus L3N Voltage (Modlon) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit: | This Modbus register is created for Modlon register mapping. Utility L3N voltage or Generator set Bus L3N voltage depending on paralleling application. | PC 3.x |
| 40757 | Customer Faults (Modlon) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | This Modbus register is created for Modlon register mapping. 16 bit fault bitmap for Modbus interface. | PC 3.x |
| 40760 | ES State (Modlon) | Read Only | 0: Standby 1: Dead Bus 2: Synchronize 3: Load Share 4: Load Goven | This Modbus register is created for Modlon register mapping. Internal paralleling status variable | PC 3.x |
| 40761 | Load Demand Stop Command (Modlon) | Read Only | 0: Inactive 1: Active | This Modbus register is created for Modlon register mapping. Modbus input for load demand stop command. | PC 3.x |
| 40764 | Genset CB Position Status (Modlon) | Read Only | 0: Open 1: Closed 2: Not Available | This Modbus register is created for Modlon register mapping. indicates generator set breaker position | PC 3.x |
| 40765 | Utility CB Position Status (Modlon) | Read Only | 0: Open 1: Closed 2: Not Available | This Modbus register is created for Modlon register mapping. indicates utility breaker position | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40766 | Remote Start Switch(Modlo n) | Read/Write | 0: Inactive 1: Active | This Modbus register is created for Modlon register mapping. Modbus Remote Start | PC 3.x |
| 40767 | Fault Reset (Modlon) | Read/Write | 0: Inactive 1: Active | This Modbus register is created for Modlon register mapping. Modbus fault reset. | PC 3.x |
| 40768 | System Network Datalink Status | Read Only | 0: Inactive 1: Active 2: Failed | Indicates communication status of the local genset on System Network (used for load demand). Available on PCC3300MLD controls only. | PC 3.x |
| 40769 | Load Demand Genset Run Hours (Upper Register value) | Read/Write | Multiplier: 1 Offset: 0 Size: 32 Sign: U Units: Hours Lower Limit: 0 Upper Limit: 999999.9 Default: 0 | Run hour accumulator used for load demand run hour equalization. This is writable. Available on PCC3300MLD controls only. | PC 3.x |
| 40770 | Load Demand Genset Run Hours (Lower Register value) | Read/Write | Multiplier: 1 Offset: 0 Size: 32 Sign: U Units: Hours Lower Limit: 0 Upper Limit: 999999.9 Default: 0 | Run hour accumulator used for load demand run hour equalization. This is writable. Available on PCC3300MLD controls only. | PC 3.x |
| 40771 | Load Demand Spare Capacity Request Status | Read Only | 0: Inactive 1: Active | Indicates the status of the spare capacity request input. When ACTIVE additional spare capacity (set by Load Demand Spare Capacity Request Value) is requested. Available on PCC3300MLD controls only. | PC 3.x |
| 40772 | System Network Termination Resistor Switch Status | Read Only | 0: On 1: Off | Indicates the status of the on- board CAN termination resistor switch (S1). Available on PCC3300MLD controls only. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40773 | Genset ID | Read/Write | 0: Gen1 9: Gen10 1: Gen2 10: Gen11 2: Gen3 11: Gen12 3: Gen4 12: Gen13 4: Gen5 13: Gen14 5: Gen6 14: Gen15 6: Gen7 15: Gen16 7: Gen8 8: Gen9 | Genset identifier. All load demand gensets must have a unique Genset ID. Available on PCC3300MLD controls only. Setup Mode must be enabled to modify the value. See Modbus Address 43343. | PC 3.x |
| 40774 | Load Demand Spare Capacity Request Value (Upper Register value) | Read/Write | Multiplier: 1 Offset: 0 Size(Bits): 32 Sign: U Units: kW Lower Limit: 0 Upper Limit: 80000 Default: 0 | Sets the kW value of additional capacity to be requested from the system when the Load Demand Spare Capacity Request Status is YES. Available on PCC3300MLD controls only. Setup Mode must be enabled to modify the value. See Modbus Address 43343. | PC 3.x |
| 40775 | Load Demand Spare Capacity Request Value (Lower Register value) | Read/Write | Multiplier: 1 Offset: 0 Size(Bits): 32 Sign: U Units: kW Lower Limit: 0 Upper Limit: 80000 Default: 0 | Sets the kW value of additional capacity to be requested from the system when the Load Demand Spare Capacity Request Status is YES. Available on PCC3300MLD controls only. Setup Mode must be enabled to modify the value. See Modbus Address 43343. | PC 3.x |
| 40776 | Load Demand Genset Enable | Read/Write | 0: Disable 1: Enable | Disables or Enables load demand on this genset only. When set to disable the genset is not included in the load demand system and can be removed without triggering a com error. Available on PCC3300MLD controls only. Setup Mode must be enabled to modify the value. See Modbus Address 43343. | PC 3.x |
| 40777 | System Settings Status | Read Only | 0: Out of Sync 1: In Sync | Indicates whether the system settings on the local genset are in sync with ones from other genset in the network. Available on PCC3300MLD controls only. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40800 | Aux101 1 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 40801 | Aux101 1 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 40802 | Aux101 1 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 40803 | Aux101 1 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 40804 | Aux101 1 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 40805 | Aux101 1 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40806 | Aux101 1 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 40807 | Aux101 1 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 40808 | Aux101 1 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 40809 | Aux101 1 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 40810 | Aux101 1 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 40811 | Aux101 1 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40812 | Aux101 1 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 40813 | Aux101 1 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 40814 | Aux101 1 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 40815 | Aux101 1 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 40816 | Aux101 1 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 40817 | Aux101 1 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40818 | Aux101 1 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 40819 | Aux101 1 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 40820 | Aux101 1 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 40821 | Aux101 1 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 40822 | Aux101 1 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 40823 | Aux101 1 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40824 | Aux101 1 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 40825 | Aux101 1 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 40826 | Aux101 1 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 40827 | Aux101 1 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 40828 | Aux101 1 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 40829 | Aux101 1 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40830 | Aux101 1 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 40831 | Aux101 1 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 40832 | Aux101 1 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 40833 | Aux101 1 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 40834 | Aux101 1 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 40835 | Aux101 1 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40836 | Aux101 1 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 40837 | Aux101 1 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 40838 | Aux101 1 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 40839 | Aux101 1 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 40840 | Aux102 0 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40841 | Aux102 0 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40842 | Aux102 0 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40843 | Aux102 0 Fault 9 Text | Read/Write | Multiplier: 1 | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40844 | Aux102 0 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40845 | Aux102 0 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40846 | Aux102 0 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40847 | Aux102 0 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40848 | Aux102 0 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40849 | Aux102 0 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40850 | Aux102 0 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40851 | Aux102 0 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40852 | Aux102 0 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40853 | Aux102 0 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40854 | Aux102 0 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40855 | Aux102 0 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40856 | Aux102 0 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40857 | Aux102 0 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40858 | Aux102 0 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40859 | Aux102 0 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40860 | Aux102 0 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40861 | Aux102 0 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40862 | Aux102 0 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40863 | Aux102 0 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40864 | Aux102 0 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40865 | Aux102 0 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40866 | Aux102 0 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40867 | Aux102 0 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40868 | Aux102 0 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40869 | Aux102 0 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40870 | Aux102 0 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40871 | Aux102 0 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40872 | Aux102 0 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40873 | Aux102 0 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40874 | Aux102 0 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40875 | Aux102 0 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40876 | Aux102 0 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40877 | Aux102 0 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40878 | Aux102 0 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40879 | Aux102 0 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40880 | Aux102 0 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40881 | Aux102 0 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40882 | Aux102 0 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40883 | Aux102 0 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40884 | Aux102 0 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40885 | Aux102 0 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40886 | Aux102 0 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40887 | Aux102 0 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40888 | Aux102 0 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40889 | Aux102 0 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40890 | Aux102 0 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40891 | Aux102 0 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40892 | Aux102 0 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40893 | Aux102 0 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40894 | Aux102 0 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40895 | Aux102 0 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40896 | Aux102 0 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40897 | Aux102 0 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40898 | Aux102 0 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40899 | Aux102 0 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40900 | Aux102 0 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40901 | Aux102 0 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40902 | Aux102 0 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40903 | Aux102 0 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40904 | Aux102 0 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40905 | Aux102 0 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40906 | Aux102 0 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40907 | Aux102 0 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40908 | Aux102 0 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40909 | Aux102 0 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40910 | Aux102 0 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40911 | Aux102 0 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40912 | Aux102 0 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40913 | Aux102 0 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40914 | Aux102 0 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40915 | Aux102 0 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40916 | Aux102 0 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40917 | Aux102 0 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40918 | Aux102 0 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40919 | Aux102 0 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40920 | Aux102 1 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40921 | Aux102 1 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40922 | Aux102 1 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40923 | Aux102 1 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40924 | Aux102 1 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40925 | Aux102 1 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40926 | Aux102 1 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40927 | Aux102 1 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40928 | Aux102 1 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40929 | Aux102 1 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40930 | Aux102 1 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40931 | Aux102 1 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40932 | Aux102 1 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40933 | Aux102 1 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40934 | Aux102 1 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40935 | Aux102 1 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40936 | Aux102 1 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40937 | Aux102 1 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40938 | Aux102 1 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40939 | Aux102 1 Fault 9 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40940 | Aux102 1 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40941 | Aux102 1 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40942 | Aux102 1 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40943 | Aux102 1 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40944 | Aux102 1 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40945 | Aux102 1 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40946 | Aux102 1 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40947 | Aux102 1 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40948 | Aux102 1 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40949 | Aux102 1 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40950 | Aux102 1 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40951 | Aux102 1 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40952 | Aux102 1 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40953 | Aux102 1 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40954 | Aux102 1 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40955 | Aux102 1 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40956 | Aux102 1 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40957 | Aux102 1 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40958 | Aux102 1 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40959 | Aux102 1 Fault 10 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40960 | Aux102 1 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40961 | Aux102 1 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40962 | Aux102 1 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40963 | Aux102 1 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40964 | Aux102 1 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40965 | Aux102 1 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40966 | Aux102 1 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40967 | Aux102 1 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40968 | Aux102 1 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40969 | Aux102 1 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40970 | Aux102 1 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40971 | Aux102 1 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40972 | Aux102 1 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40973 | Aux102 1 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40974 | Aux102 1 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40975 | Aux102 1 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40976 | Aux102 1 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40977 | Aux102 1 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40978 | Aux102 1 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40979 | Aux102 1 Fault 11 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40980 | Aux102 1 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40981 | Aux102 1 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40982 | Aux102 1 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40983 | Aux102 1 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40984 | Aux102 1 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40985 | Aux102 1 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40986 | Aux102 1 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40987 | Aux102 1 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40988 | Aux102 1 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40989 | Aux102 1 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40990 | Aux102 1 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40991 | Aux102 1 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40992 | Aux102 1 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40993 | Aux102 1 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40994 | Aux102 1 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40995 | Aux102 1 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40996 | Aux102 1 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 40997 | Aux102 1 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40998 | Aux102 1 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 40999 | Aux102 1 Fault 12 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 41000 | Load Demand System Enable | Read/Write | 0: Disable 1: Enable | Disables or Enables load demand operation of all connected gensets. Available on PCC3300MLD controls only. | PC 3.x |
| 41001 | Load Demand Type | Read/Write | 0: Run Hours Equalization (Run Hr Eql) 1: Fixed Sequence (Fixed Seq) | Sets the sequencing priority for load demand. Available on PCC3300MLD controls only. | PC 3.x |
| 41002 | Load Demand Threshold Method | Read/Write | 0: kW 1: %kW | Sets whether the load demand start/stop control is based on a relative (%) or absolute (kW) threshold. Available on PCC3300MLD controls only. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 41003 | Load Demand Start Threshold (%kW) | Read/Write | Multiplier: 1 Offset: 0 Size(Bits): 8 Sign: U Units: % Lower Limit: 25 Upper Limit: 100 Default: 80 | When the ratio of load to capacity is greater than this value the next genset will start. Must be greater than Load Demand Stop Threshold by at least 5%. Available on PCC3300MLD controls only. | PC 3.x |
| 41004 | Load Demand Start Threshold (kW) | Read/Write | Multiplier: 1 Offset: 0 Size(Bits): 16 Sign: U Units: kW Lower Limit: 5 Upper Limit: 5000 Default: 500 | When surplus capacity is less than this value the next genset will start. Must be less than Load Demand Stop Threshold (kW). Available on PCC3300MLD controls only. | PC 3.x |
| 41005 | Load Demand Stop Threshold (%kW) | Read/Write | Multiplier: 1 Offset: 0 Size(Bits): 8 Sign: U Units: % Lower Limit: 20 Upper Limit: 95 Default: 60 | When the ratio of load to capacity is less than this value the next genset will stop. Must be less than Load Demand Start Threshold by at least 5%. Available on PCC3300MLD controls only. | PC 3.x |
| 41006 | Load Demand Stop Threshold (kW) | Read/Write | Multiplier: 1 Offset: 0 Size(Bits): 16 Sign: U Units: kW Lower Limit: 5 Upper Limit: 5000 Default: 1000 | When surplus capacity is greater than this value the next genset will stop. Must be greater than Load Demand Start Threshold (kW). Available on PCC3300MLD controls only. | PC 3.x |
| 41007 | Load Demand Run Hours Differential | Read/Write | Multiplier: 1 Offset: 0 Size(Bits): 16 Sign: U Units: Hours Lower Limit: 1 Upper Limit: 250 Default: 50 | When the difference between Load Demand Genset Run Hours between any running genset and any stopped genset reaches this value the stopped genset will be started. Available on PCC3300MLD controls only. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 41008 | Load Demand Genset Fail Delay | Read/Write | Multiplier: 1 Offset: 0 Size(Bits): 16 Sign: U Units: seconds Lower Limit: 10 Upper Limit: 900 Default: 60 | Sets the time delay that the system waits for a genset to come online before declaring it as failed. Available on PCC3300MLD controls only. | PC 3.x |
| 41009 | Load Demand Initial Delay | Read/Write | Multiplier: 1 Offset: 0 Size(Bits): 16 Sign: U Units: seconds Lower Limit: 60 Upper Limit: 1500 Default: 300 | Sets the time delay before gensets are allowed to stop after initial start or after resuming halted load demand. Available on PCC3300MLD controls only. | PC 3.x |
| 41010 | Load Demand Start Delay | Read/Write | Multiplier: 1 Offset: 0 Size(Bits): 16 Sign: U Units: seconds Lower Limit: 0 Upper Limit: 1500 Default: 10 | Sets the time delay before next genset is allowed to start. Available on PCC3300MLD controls only. | PC 3.x |
| 41011 | Load Demand Stop Delay | Read/Write | Multiplier: 1 Offset: 0 Size(Bits): 16 Sign: U Units: seconds Lower Limit: 60 Upper Limit: 1500 Default: 300 | Sets the time delay before next genset is allowed to stop. Available on PCC3300MLD controls only. | PC 3.x |
| 41012 | Clear Lost Gensets Local | Read/Write | 0: No 1: Yes | When set to YES all gensets in state ”Lost” will change to state ”Gen Does Not Exist” in order to clear Lost Genset Warning. Available on PCC3300MLD controls only. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 41013 | Load Demand Fixed Priority 1 | Read/Write | 0: Gen1 1: Gen2 2: Gen3 3: Gen4 4: Gen5 5: Gen6 6: Gen7 7: Gen8 8: Gen9 9: Gen10 10: Gen11 11: Gen12 12: Gen13 13: Gen14 14: Gen15 15: Gen16 | Assigns a genset to fixed priority 1. Used when Load Demand Type is set to Fixed Sequence. Available on PCC3300MLD controls only. | PC 3.x |
| 41014 | Load Demand Fixed Priority 2 | Read/Write | 0: Gen1 1: Gen2 2: Gen3 3: Gen4 4: Gen5 5: Gen6 6: Gen7 7: Gen8 8: Gen9 9: Gen10 10: Gen11 11: Gen12 12: Gen13 13: Gen14 14: Gen15 15: Gen16 | Assigns a genset to fixed priority 2. Used when Load Demand Type is set to Fixed Sequence. Available on PCC3300MLD controls only. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 41015 | Load Demand Fixed Priority 3 | Read/Write | 0: Gen1 1: Gen2 2: Gen3 3: Gen4 4: Gen5 5: Gen6 6: Gen7 7: Gen8 8: Gen9 9: Gen10 10: Gen11 11: Gen12 12: Gen13 13: Gen14 14: Gen15 15: Gen16 | Assigns a genset to fixed priority 3. Used when Load Demand Type is set to Fixed Sequence. Available on PCC3300MLD controls only. | PC 3.x |
| 41016 | Load Demand Fixed Priority 4 | Read/Write | 0: Gen1 1: Gen2 2: Gen3 3: Gen4 4: Gen5 5: Gen6 6: Gen7 7: Gen8 8: Gen9 9: Gen10 10: Gen11 11: Gen12 12: Gen13 13: Gen14 14: Gen15 15: Gen16 | Assigns a genset to fixed priority 4. Used when Load Demand Type is set to Fixed Sequence. Available on PCC3300MLD controls only. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 41017 | Load Demand Fixed Priority 5 | Read/Write | 0: Gen1 1: Gen2 2: Gen3 3: Gen4 4: Gen5 5: Gen6 6: Gen7 7: Gen8 8: Gen9 9: Gen10 10: Gen11 11: Gen12 12: Gen13 13: Gen14 14: Gen15 15: Gen16 | Assigns a genset to fixed priority 5. Used when Load Demand Type is set to Fixed Sequence. Available on PCC3300MLD controls only. | PC 3.x |
| 41018 | Load Demand Fixed Priority 6 | Read/Write | 0: Gen1 1: Gen2 2: Gen3 3: Gen4 4: Gen5 5: Gen6 6: Gen7 7: Gen8 8: Gen9 9: Gen10 10: Gen11 11: Gen12 12: Gen13 13: Gen14 14: Gen15 15: Gen16 | Assigns a genset to fixed priority 6. Used when Load Demand Type is set to Fixed Sequence. Available on PCC3300MLD controls only. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 41019 | Load Demand Fixed Priority 7 | Read/Write | 0: Gen1 1: Gen2 2: Gen3 3: Gen4 4: Gen5 5: Gen6 6: Gen7 7: Gen8 8: Gen9 9: Gen10 10: Gen11 11: Gen12 12: Gen13 13: Gen14 14: Gen15 15: Gen16 | Assigns a genset to fixed priority 7. Used when Load Demand Type is set to Fixed Sequence. Available on PCC3300MLD controls only. | PC 3.x |
| 41020 | Load Demand Fixed Priority 8 | Read/Write | 0: Gen1 1: Gen2 2: Gen3 3: Gen4 4: Gen5 5: Gen6 6: Gen7 7: Gen8 8: Gen9 9: Gen10 10: Gen11 11: Gen12 12: Gen13 13: Gen14 14: Gen15 15: Gen16 | Assigns a genset to fixed priority 8. Used when Load Demand Type is set to Fixed Sequence. Available on PCC3300MLD controls only. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 41021 | Load Demand Fixed Priority 9 | Read/Write | 0: Gen1 1: Gen2 2: Gen3 3: Gen4 4: Gen5 5: Gen6 6: Gen7 7: Gen8 8: Gen9 9: Gen10 10: Gen11 11: Gen12 12: Gen13 13: Gen14 14: Gen15 15: Gen16 | Assigns a genset to fixed priority 9. Used when Load Demand Type is set to Fixed Sequence. Available on PCC3300MLD controls only. | PC 3.x |
| 41022 | Load Demand Fixed Priority 10 | Read/Write | 0: Gen1 1: Gen2 2: Gen3 3: Gen4 4: Gen5 5: Gen6 6: Gen7 7: Gen8 8: Gen9 9: Gen10 10: Gen11 11: Gen12 12: Gen13 13: Gen14 14: Gen15 15: Gen16 | Assigns a genset to fixed priority 10. Used when Load Demand Type is set to Fixed Sequence. Available on PCC3300MLD controls only. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 41023 | Load Demand Fixed Priority 11 | Read/Write | 0: Gen1 1: Gen2 2: Gen3 3: Gen4 4: Gen5 5: Gen6 6: Gen7 7: Gen8 8: Gen9 9: Gen10 10: Gen11 11: Gen12 12: Gen13 13: Gen14 14: Gen15 15: Gen16 | Assigns a genset to fixed priority 11. Used when Load Demand Type is set to Fixed Sequence. Available on PCC3300MLD controls only. | PC 3.x |
| 41024 | Load Demand Fixed Priority 12 | Read/Write | 0: Gen1 1: Gen2 2: Gen3 3: Gen4 4: Gen5 5: Gen6 6: Gen7 7: Gen8 8: Gen9 9: Gen10 10: Gen11 11: Gen12 12: Gen13 13: Gen14 14: Gen15 15: Gen16 | Assigns a genset to fixed priority 12. Used when Load Demand Type is set to Fixed Sequence. Available on PCC3300MLD controls only. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 41025 | Load Demand Fixed Priority 13 | Read/Write | 0: Gen1 1: Gen2 2: Gen3 3: Gen4 4: Gen5 5: Gen6 6: Gen7 7: Gen8 8: Gen9 9: Gen10 10: Gen11 11: Gen12 12: Gen13 13: Gen14 14: Gen15 15: Gen16 | Assigns a genset to fixed priority 13. Used when Load Demand Type is set to Fixed Sequence. Available on PCC3300MLD controls only. | PC 3.x |
| 41026 | Load Demand Fixed Priority 14 | Read/Write | 0: Gen1 1: Gen2 2: Gen3 3: Gen4 4: Gen5 5: Gen6 6: Gen7 7: Gen8 8: Gen9 9: Gen10 10: Gen11 11: Gen12 12: Gen13 13: Gen14 14: Gen15 15: Gen16 | Assigns a genset to fixed priority 14. Used when Load Demand Type is set to Fixed Sequence. Available on PCC3300MLD controls only. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 41027 | Load Demand Fixed Priority 15 | Read/Write | 0: Gen1 1: Gen2 2: Gen3 3: Gen4 4: Gen5 5: Gen6 6: Gen7 7: Gen8 8: Gen9 9: Gen10 10: Gen11 11: Gen12 12: Gen13 13: Gen14 14: Gen15 15: Gen16 | Assigns a genset to fixed priority 15. Used when Load Demand Type is set to Fixed Sequence. Available on PCC3300MLD controls only. | PC 3.x |
| 41028 | Load Demand Fixed Priority 16 | Read/Write | 0: Gen1 1: Gen2 2: Gen3 3: Gen4 4: Gen5 5: Gen6 6: Gen7 7: Gen8 8: Gen9 9: Gen10 10: Gen11 11: Gen12 12: Gen13 13: Gen14 14: Gen15 15: Gen16 | Assigns a genset to fixed priority 16. Used when Load Demand Type is set to Fixed Sequence. Available on PCC3300MLD controls only. | PC 3.x |
| 41029 | System Network Remote Fault Reset | Read/Write | 0: Inactive 1: Active | When set to YES all the system network faults in the system would be reset. Available on PCC3300MLD controls only. | PC 3.x |
| 41030 | Synchronize System Settings | Read/Write | 0: No 1: Yes | When set to YES system settings from the genset will be broadcasted and synchronized to all other gensets in the network. Available on PCC3300MLD controls only. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 41031 | Battery Charger 2 Failed Switch | Read Only | 0: Inactive 1: Active | Battery Charger 2 Failed Switch function output status; gives software Inactive/Active state | PC 3.x |
| 41032 | Battery Charger 3 Failed Switch | Read Only | 0: Inactive 1: Active | Battery Charger 3 Failed Switch function output status; gives software Inactive/Active state | PC 3.x |
| 41033 | Battery Charger 4 Failed Switch | Read Only | 0: Inactive 1: Active | Battery Charger 4 Failed Switch function output status; gives software Inactive/Active state | PC 3.x |
| 41034 | Intake Air Restriction Indicator 1 fault switch | Read Only | 0: Inactive 1: Active | Intake Air Restriction Indicator 1 fault switch function output status; gives software Inactive/Active state | PC 3.x |
| 41035 | Intake Air Restriction Indicator 2 fault switch | Read Only | 0: Inactive 1: Active | Intake Air Restriction Indicator 2 fault switch function output status; gives software Inactive/Active state | PC 3.x |
| 41036 | Intake Air Restriction Indicator 3 fault switch | Read Only | 0: Inactive 1: Active | Intake Air Restriction Indicator 3 fault switch function output status; gives software Inactive/Active state | PC 3.x |
| 41037 | Intake Air Restriction Indicator 4 fault switch | Read Only | 0: Inactive 1: Active | Intake Air Restriction Indicator 4 fault switch function output status; gives software Inactive/Active state | PC 3.x |
| 41038 | Starter Air Supply Pressure Low Fault Switch | Read Only | 0: Inactive 1: Active | Starter Air Supply Pressure Low Fault Switch function output status; gives software Inactive/Active | PC 3.x |
| 41039 | Starter Air Tank Volume Low Fault Switch | Read Only | 0: Inactive 1: Active | Starter Air Tank Volume Low Fault Switch function output status; gives software Inactive/Active state | PC 3.x |
| 41300 | AmpSentry Maintenance Mode Status | Read Only | 0: Inactive 1: Active | A protection mode that causes the alternator to shutdown instantly when a short circuit is detected. Used to limit arc flash energy with personnel working | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 41301 | AMM PC Tool Detected | Read Only | 0: Inactive 1: Active | Detects whether any service tool is connected via TB15 or J14 by validating if a read/write command has been exchanged via MON using a five second decremental timer. If the timer expires, then it is determine service tool is no longer connected. | PC 3.x |
| 41302 | AMM Disable Walkaway Timer Value | Read Only | Multiplier : 1 Units: Seconds Offset: 0 Lower Limit: NA Size (Bits) : 16 Upper Limit: NA Sign: U Default: NA | Countdown timer when walkaway is complete. | PC 3.x |
| 41400 | Fault Status Bitmap 31 | Read Only | Multiplier : 1 Units: NA Offset: 0 Lower Limit: 0 Size (Bits) : 16 Upper Limit: 65535 Sign: U Default: NA | 16 bit fault bitmap for Modbus interface. | PC 3.x |
| 41401 | Fault Status Bitmap 33 | Read Only | Multiplier : 1 Units: NA Offset: 0 Lower Limit: 0 Size (Bits) : 16 Upper Limit: 65535 Sign: U Default: NA | 16 bit Diesel Fault Bitmap for Modbus interface | PC 3.x |
| 41402 | Fault Status Bitmap 34 | Read Only | Multiplier : 1 Units: NA Offset: 0 Lower Limit: 0 Size (Bits) : 16 Upper Limit: 65535 Sign: U Default: NA | 16 bit Diesel Fault Bitmap for Modbus interface | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 41403 | AT Fault Status Bitmap 2 | Read Only | Multiplier : 1 Units: NA Offset: 0 Lower Limit: 0 Size (Bits) : 16 Upper Limit: 65535 Sign: U Default: NA | 16 bit AT Fault Bitmap for Modbus interface | PC 3.x |
| 41404 | AT Fault Status Bitmap 3 | Read Only | Multiplier : 1 Units: NA Offset: 0 Lower Limit: 0 Size (Bits) : 16 Upper Limit: 65535 Sign: U Default: NA | 16 bit AT Fault Bitmap for Modbus interface | PC 3.x |
| 41405 | AT Fault Status Bitmap 4 | Read Only | Multiplier : 1 Units: NA Offset: 0 Lower Limit: 0 Size (Bits) : 16 Upper Limit: 65535 Sign: U Default: NA | 16 bit AT Fault Bitmap for Modbus interface | PC 3.x |
| 41406 | AT Fault Status Bitmap 5 | Read Only | Multiplier : 1 Units: NA Offset: 0 Lower Limit: 0 Size (Bits) : 16 Upper Limit: 65535 Sign: U Default: NA | 16 bit AT Fault Bitmap for Modbus interface | PC 3.x |
| 41407 | AT Fault Status Bitmap 6 | Read Only | Multiplier : 1 Units: NA Offset: 0 Lower Limit: 0 Size (Bits) : 16 Upper Limit: 65535 Sign: U Default: NA | 16 bit AT Fault Bitmap for Modbus interface | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 41408 | AT Fault Status Bitmap 7 | Read Only | Multiplier : 1 Units: NA Offset: 0 Lower Limit: 0 Size (Bits) : 16 Upper Limit: 65535 Sign: U Default: NA | 16 bit AT Fault Bitmap for Modbus interface | PC 3.x |
| 41409 | AT Fault Status Bitmap 8 | Read Only | Multiplier : 1 Units: NA Offset: 0 Lower Limit: 0 Size (Bits) : 16 Upper Limit: 65535 Sign: U Default: NA | 16 bit AT Fault Bitmap for Modbus interface | PC 3.x |
| 41416 | Fault Status Bitmap 35 | Read Only | Multiplier : 1 Units: NA Offset: 0 Lower Limit: 0 Size (Bits) : 16 Upper Limit: 65535 Sign: U Default: NA | 16 bit Diesel Fault Bitmap for Modbus interface | PC 3.x |
| 41417 | Fault Status Bitmap 36 | Read Only | Multiplier : 1 Units: NA Offset: 0 Lower Limit: 0 Size (Bits) : 16 Upper Limit: 65535 Sign: U Default: NA | 16 bit Diesel Fault Bitmap for Modbus interface | PC 3.x |
| 41418 | Fault Status Bitmap 37 | Read Only | Multiplier : 1 Units: NA Offset: 0 Lower Limit: 0 Size (Bits) : 16 Upper Limit: 65535 Sign: U Default: NA | 16 bit Diesel Fault Bitmap for Modbus interface | PC 3.x |
| 42000 | Load Demand State | Read Only | 0: Off 1: Halted 2: Initial Delay 3: Load Monitor | Indicates the status of Load Demand operation. Available on PCC3300MLD controls only. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 42001 | Load Demand Genset Bus Total kW (Upper Register value) | Read Only | Multiplier: 1.0 Offset: 0 Size (bits): 32 Sign: U Units: kW Lower Limit: 0 Upper Limit: 80000 Default: 0 | Indicates the total load of System Network connected gensets. Available on PCC3300MLD controls only. | PC 3.x |
| 42002 | Load Demand Genset Bus Total kW (Lower Register value) | Read Only | Multiplier: 1.0 Offset: 0 Size (bits): 32 Sign: U Units: kW Lower Limit: 0 Upper Limit: 80000 Default: 0 | Indicates the total load of System Network connected gensets. Available on PCC3300MLD controls only. | PC 3.x |
| 42003 | Load Demand Surplus Capacity (Upper Register value) | Read Only | Multiplier: 1.0 Offset: 0 Size (bits): 32 Sign: U Units: kW Lower Limit: 0 Upper Limit: 80000 Default: 0 | Indicates the total load of System Network connected gensets. Available on PCC3300MLD controls only. | PC 3.x |
| 42004 | Load Demand Surplus Capacity (Lower Register value) | Read Only | Multiplier: 1.0 Offset: 0 Size (bits): 32 Sign: U Units: kW Lower Limit: 0 Upper Limit: 80000 Default: 0 | Indicates the total load of System Network connected gensets. Available on PCC3300MLD controls only. | PC 3.x |
| 42005 | Load Demand Online Capacity (Upper Register value) | Read Only | Multiplier: 1.0 Offset: 0 Size (bits): 32 Sign: U Units: kW Lower Limit: 0 Upper Limit: 80000 Default: 0 | Indicates the total amount of online kW bus capacity for load demand. Only gensets which are eligible for load demand are counted. Available on PCC3300MLD controls only. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 42006 | Load Demand Online Capacity (Lower Register value) | Read Only | Multiplier: 1.0 Offset: 0 Size (bits): 32 Sign: U Units: kW Lower Limit: 0 Upper Limit: 80000 Default: 0 | Indicates the total amount of online kW bus capacity for load demand. Only gensets which are eligible for load demand count. Available on PCC3300MLD controls only. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 42007 | Load Demand Initial Delay Timer | Read Only | Multiplier: 1.0 Offset: 0 Size (bits): 16 Sign: U Units: Seconds Lower Limit: 0 Upper Limit: 1500 Default: 0 | Indicates the time remaining before gensets are allowed to stop after initial start or after resuming halted load demand. This timer is set by Load Demand Initial Delay. Available on PCC3300MLD controls only. | PC 3.x |
| 42008 | Load Demand Start Delay Timer | Read Only | Multiplier: 1.0 Offset: 0 Size (bits): 16 Sign: U Units: Seconds Lower Limit: 0 Upper Limit: 1500 Default: 0 | Indicates the time remaining before next genset is allowed to start. This timer is set by Load Demand Start Delay. Available on PCC3300MLD controls only. | PC 3.x |
| 42009 | Load Demand Stop Delay Timer | Read Only | Multiplier: 1.0 Offset: 0 Size (bits): 16 Sign: U Units: Seconds Lower Limit: 0 Upper Limit: 1500 Default: 0 | Indicates the time remaining before next genset is allowed to stop. This timer is set by Load Demand Stop Delay. Available on PCC3300MLD controls only. | PC 3.x |
| 42010 | Load Demand Spare Capacity Available | Read Only | 0: No 1: Yes | Indicates when the current load and spare capacity requirements are satisfied. Available on PCC3300MLD controls only. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 42011 | Load Demand Total Spare Capacity Requested (Upper Register value) | Read Only | Multiplier: 1.0 Offset: 0 Size (bits): 32 Sign: U Units: kW Lower Limit: 0 Upper Limit: 80000 Default: 0 | Indicates the total kW value of all currently active spare capacity requests in the system. Available on PCC3300MLD controls only. | PC 3.x |
| 42012 | Load Demand Total Spare Capacity Requested (Lower Register value) | Read Only | Multiplier: 1.0 Offset: 0 Size (bits): 32 Sign: U Units: kW Lower Limit: 0 Upper Limit: 80000 Default: 0 | Indicates the total kW value of all currently active spare capacity requests in the system. Available on PCC3300MLD controls only. | PC 3.x |
| 42013 | Load Demand Next Start Threshold (kW) (Upper Register value) | Read Only | Multiplier: 1.0 Offset: 0 Size (bits): 32 Sign: U Units: kW Lower Limit: 0 Upper Limit: 80000 Default: 0 | The kW load at which the next genset will be started. Available on PCC3300MLD controls only. | PC 3.x |
| 42014 | Load Demand Next Start Threshold (kW) (Lower Register value) | Read Only | Multiplier: 1.0 Offset: 0 Size (bits): 32 Sign: U Units: kW Lower Limit: 0 Upper Limit: 80000 Default: 0 | The kW load at which the next genset will be started. Available on PCC3300MLD controls only. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 42015 | Load Demand Next Stop Threshold (Upper Register value) | Read Only | Multiplier: 1.0 Offset: 0 Size (bits): 32 Sign: U Units: kW Lower Limit: 0 Upper Limit: 80000 Default: 0 | The kW load at which the next genset will be stopped. Available on PCC3300MLD controls only. | PC 3.x |
| 42016 | Load Demand Next Stop Threshold (Lower Register value) | Read Only | Multiplier: 1.0 Offset: 0 Size (bits): 32 Sign: U Units: kW Lower Limit: 0 Upper Limit: 80000 Default: 0 | The kW load at which the next genset will be stopped. Available on PCC3300MLD controls only. | PC 3.x |
| 42017 | Load Demand Next Gen to start (kW) | Read Only | 0: Gen1 1: Gen2 2: Gen3 3: Gen4 4: Gen5 5: Gen6 6: Gen7 7: Gen8 8: Gen9 9: Gen10 10: Gen11 11: Gen12 12: Gen13 13: Gen14 14: Gen15 15: Gen16 | Indicates the next genset to start by ID. Available on PCC3300MLD controls only. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 42018 | Load Demand Next Gen to Stop | Read Only | 0: Gen1 1: Gen2 2: Gen3 3: Gen4 4: Gen5 5: Gen6 6: Gen7 7: Gen8 8: Gen9 9: Gen10 10: Gen11 11: Gen12 12: Gen13 13: Gen14 14: Gen15 15: Gen16 | Indicates the next genset to stop by ID. Available on PCC3300MLD controls only. | PC 3.x |
| 42019 | Load Demand Inhibit Local | Read Only | 0: Inactive 1: Active | Indicates the status of the Load Demand Inhibit input. When ACTIVE all the gensets will start. Available on PCC3300MLD controls only. | PC 3.x |
| 43000 | Genset % Application L1 Current | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: % Lower Limit: Upper Limit: | Monitors the generator set application L1 current percentage output. | PC 2.x, PC 3.x |
| 43001 | Genset % Application L2 Current | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: % Lower Limit: Upper Limit: | Monitors the generator set application L2 current percentage output. | PC 2.x, PC 3.x |
| 43002 | Genset % Application L1 kVA | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: % Lower Limit: Upper Limit: | Monitors the generator set application L1 kVA percentage output. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43003 | Genset % Application L3 Current | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: % Lower Limit: Upper Limit: | Monitors the generator set application L3 current percentage output. | PC 2.x, PC 3.x |
| 43004 | Genset % Application L2 kVA | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: % Lower Limit: Upper Limit: | Monitors the generator set application L2 kVA percentage output. | PC 2.x, PC 3.x |
| 43005 | Genset % Application L3 kVA | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: % Lower Limit: Upper Limit: | Monitors the generator set application L3 kVA percentage output. | PC 2.x, PC 3.x |
| 43006 | Genset % Application L1 kW | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: % Lower Limit: Upper Limit: | Monitors the generator set application L1 KW percentage output. | PC 2.x, PC 3.x |
| 43007 | Genset % Application L2 kW | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: % Lower Limit: Upper Limit: | Monitors the generator set application L2 KW percentage output. | PC 2.x, PC 3.x |
| 43008 | Genset % Application L3 kW | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: % Lower Limit: Upper Limit: | Monitors the generator set application L3 KW percentage output. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43009 | Genset % Application Total kVA | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: % Lower Limit: Upper Limit: | Monitors the total generator set application kVA percentage output. | PC 2.x, PC 3.x |
| 43010 | Genset % Application Total kW | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: % Lower Limit: Upper Limit: | Monitors the total generator set application KW percentage output. | PC 2.x, PC 3.x |
| 43011 | Genset % Standby L1 kVA | Read Only | Multiplier : 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: % Lower Limit: NA Upper Limit: NA | Monitors the genset standby L1 kVA percentage output. | PC 2.x, PC 3.x |
| 43012 | Genset % Standby L3 kVA | Read Only | Multiplier : 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: % Lower Limit: NA Upper Limit: NA | Monitors the genset standby L3 kVA percentage output. | PC 2.x, PC 3.x |
| 43013 | Genset % Standby L2 kVA | Read Only | Multiplier : 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: % Lower Limit: NA Upper Limit: NA Default: NA | Monitors the genset standby L2 kVA percentage output. | PC 2.x, PC 3.x |
| 43014 | Genset % Standby L1 kW | Read Only | Multiplier : 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: % Lower Limit: NA Upper Limit: NA Default: NA | Monitors the genset standby L1 KW percentage output. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43015 | Genset % Standby L2 kW | Read Only | Multiplier : 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: % Lower Limit: NA Upper Limit: NA Default: NA | Monitors the genset standby L2 KW percentage output. | PC 2.x, PC 3.x |
| 43016 | Genset % Standby L3 kW | Read Only | Multiplier : 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: % Lower Limit: NA Upper Limit: NA Default: NA | Monitors the genset standby L3 KW percentage output. | PC 2.x, PC 3.x |
| 43017 | Genset % Standby Total kVA | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: % Lower Limit: Upper Limit: | Monitors the total generator set standby kVA percentage output. | PC 2.x, PC 3.x |
| 43018 | Genset Application kVA rating | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: kVA Lower Limit: Upper Limit: | The generator set kVA rating. | PC 2.x, PC 3.x |
| 43019 | Genset Application kW rating | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: kW Lower Limit: Upper Limit: | The generator set KW rating. | PC 2.x, PC 3.x |
| 43020 | Genset Application Nominal Current | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Amps Lower Limit: Upper Limit: | The value of the generator set application nominal current. Displayed as ”Generator set Application Rated Current” in HMI | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43021 | Genset Average Voltage% | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: U Unit: % Lower Limit: Upper Limit: | Generator set average voltage percentage. | PC 2.x, PC 3.x |
| 43030 | Genset L1 Power Factor | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 8 Sign: S Unit: PF Lower Limit: Upper Limit: | Generator set L1 power factor | PC 2.x, PC 3.x |
| 43031 | Genset L1L2 Phase Difference | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: U Unit: Degrees Lower Limit: Upper Limit: | Generator set L1L2 voltage phase angle | PC 2.x, PC 3.x |
| 43032 | Genset L1L2 Voltage% | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: U Unit: % Lower Limit: Upper Limit: | Generator set L1L2 voltage% | PC 2.x, PC 3.x |
| 43033 | Genset L1N Voltage% | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: U Unit: % Lower Limit: Upper Limit: | Generator set L1N voltage% | PC 2.x, PC 3.x |
| 43044 | Genset L2 Power Factor | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 8 Sign: S Unit: PF Lower Limit: -1.28 Upper Limit: 1.27 | Generator set L2 power factor | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43045 | Genset L2L3 Phase Difference | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 8 Sign: U Unit: Degrees Lower Limit: 0 Upper Limit: 655.3 | Generator set L2L3 voltage phase angle | PC 2.x, PC 3.x |
| 43046 | Genset L2L3 Voltage% | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: U Unit: % Lower Limit: Upper Limit: | Generator set L2L3 voltage% | PC 2.x, PC 3.x |
| 43047 | Genset L2N Voltage% | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: U Unit: % Lower Limit: 0 Upper Limit: 655.3 | Generator set L2N voltage% | PC 2.x, PC 3.x |
| 43058 | Genset L3 Power Factor | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 8 Sign: S Unit: PF Lower Limit: -1.28 Upper Limit: 1.22 | Generator set L3 power factor | PC 2.x, PC 3.x |
| 43059 | Genset L3L1 Phase Difference | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 8 Sign: U Unit: Degrees Lower Limit: 0 Upper Limit: 655.3 | Generator set L3L1 voltage phase angle | PC 2.x, PC 3.x |
| 43060 | Genset L3L1 Voltage% | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: U Unit: % Lower Limit: 0 Upper Limit: 655.3 | Generator set L3L1 voltage% | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43061 | Genset L3N Voltage% | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: U Unit: % Lower Limit: Upper Limit: | Generator set L3N voltage% | PC 2.x, PC 3.x |
| 43062 | Genset Standby kVA rating | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: kVA Lower Limit: Upper Limit: | kVA rating for the generator set in Standby configuration. | PC 2.x, PC 3.x |
| 43063 | Genset Standby kW rating | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: kW Lower Limit: Upper Limit: | KW rating for the generator set in Standby configuration. | PC 2.x, PC 3.x |
| 43064 | Genset Standby Nominal Current | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Amps Lower Limit: Upper Limit: | The value of the generator set standby nominal current. Displayed as ”Generator set Standby Rated Current” in HMI | PC 2.x, PC 3.x |
| 43065 | Genset Total kVAh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: kVAh Lower Limit: Upper Limit: | Generator set total kVAh accumulation | PC 2.x, PC 3.x |
| 43066 | Genset Total kVAh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: kVAh Lower Limit: Upper Limit: | Generator set total kVAh accumulation | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43067 | Genset Total kVARs per Standby kVA | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: S Unit: % Lower Limit: Upper Limit: | Total kVAR’s per Standby kVA. | PC 2.x, PC 3.x |
| 43100 | Genset Bus Average Voltage% | Read Only | Multiplier : 0.01 Offset: 0 Size (bits): 16 Sign: U Unit: % Lower Limit: NA Upper Limit: NA Default: NA | Genset Bus average voltage% | PC 3.x |
| 43111 | Genset Bus L1 Power Factor | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 8 Sign: S Unit: PF Lower Limit: -1.28 Upper Limit: 1.22 | Generator set Bus L1 power factor | PC 3.x |
| 43112 | Genset Bus L1L2 Phase Difference | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: U Unit: Degrees Lower Limit: Upper Limit: | Generator set bus L1L2 voltage phase angle | PC 3.x |
| 43113 | Genset Bus L1L2 Voltage% | Read Only | Multiplier : 0.01 Offset: 0 Size (bits): 16 Sign: U Units: % Lower Limit: NA Upper Limit: NA | Genset Bus L1L2 voltage% | PC 3.x |
| 43114 | Genset Bus L1N Voltage% | Read Only | Multiplier : 0.01 Offset: 0 Size (bits): 16 Sign: U Units: % Lower Limit: NA Upper Limit: NA Default: NA | Genset Bus L1N voltage% | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43125 | Genset Bus L2 Power Factor | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 8 Sign: S Unit: PF Lower Limit: NA Upper Limit: NA | Generator set Bus L2 power factor | PC 3.x |
| 43126 | Genset Bus L2L3 Phase Difference | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: U Unit: Degrees Lower Limit: NA Upper Limit: NA | Generator set bus L2L3 voltage phase angle | PC 3.x |
| 43127 | Genset Bus L2L3 Voltage% | Read Only | Multiplier : 0.01 Offset: 0 Size (bits): 16 Sign: U Units: % Lower Limit: NA Upper Limit: NA Default: NA | Genset Bus L2L3 voltage% | PC 3.x |
| 43128 | Genset Bus L2N Voltage% | Read Only | Multiplier : 0.01 Offset: 0 Size (bits): 16 Sign: U Units: % Lower Limit: NA Upper Limit: NA Default: NA | Genset Bus L2N voltage% | PC 3.x |
| 43139 | Genset Bus L3 Power Factor | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 8 Sign: S Unit: PF Lower Limit: -1.28 Upper Limit: 1.22 | Generator set Bus L3 power factor | PC 3.x |
| 43140 | Genset Bus L3L1 Phase Difference | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: U Unit: Degrees Lower Limit: Upper Limit: | Generator set bus L3L1 voltage phase angle | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43141 | Genset Bus L3L1 Voltage% | Read Only | Multiplier : 0.01 Offset: 0 Size (bits): 16 Sign: U Units: % Lower Limit: NA Upper Limit: NA Default: NA | Genset Bus L3L1 voltage% | PC 3.x |
| 43142 | Genset Bus L3N Voltage% | Read Only | Multiplier : 0.01 Offset: 0 Size (bits): 16 Sign: U Units: % Lower Limit: NA Upper Limit: NA Default: NA | Genset Bus L3N voltage% | PC 3.x |
| 43143 | Genset Bus Total kVAh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: kVAh Lower Limit: Upper Limit: Default: NA | Generator set bus total kVAh accumulation | PC 3.x |
| 43144 | Genset Bus Total kVAh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: kVAh Lower Limit: Upper Limit: | Generator set bus total kVAh accumulation | PC 3.x |
| 43145 | Sync Phase Difference | Read Only | Multiplier : 0.01 Offset: 0 Size (bits): 16 Sign: S Units: deg Lower Limit: NA Upper Limit: NA Default: NA | Other meter to genset meter L1 voltage phase angle | PC 3.x |
| 43146 | Paralleling Application | Read/Write | 0: None 1: Utility 2: Genset Bus | Determines what the function of the Other Meter is. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43147 | System Total kVA | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: kVA Lower Limit: NA Upper Limit: NA Default: NA | Sum of genset bus and utility bus kVA | PC 3.x |
| 43148 | System Total kVAR | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: S Units: kVAR Lower Limit: NA Upper Limit: NA Default: NA | Sum of genset bus and utility bus kVAR | PC 3.x |
| 43149 | System Total kW | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: kW Lower Limit: NA Upper Limit: NA Default: NA | Sum of genset bus and utility bus kW | PC 3.x |
| 43150 | System Total Power Factor | Read Only | Multiplier : 0.01 Offset: 0 Size (bits): 8 Sign: U Units: PF Lower Limit: NA Upper Limit: NA Default: NA | System total power factor (totalized value of utility bus plus genset bus) | PC 3.x |
| 43151 | Utility Average Voltage% | Read Only | Multiplier : 0.01 Offset: 0 Size (bits): 16 Sign: U Units: % Lower Limit: NA Upper Limit: NA Default: NA | Utility average voltage% | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43162 | Utility L1 Power Factor | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 8 Sign: S Unit: PF Lower Limit: NA Upper Limit: NA | Utility L1 power factor | PC 3.x |
| 43163 | Utility L1L2 Phase Difference | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: U Unit: Degrees Lower Limit: NA Upper Limit: NA | Utility L1L2 voltage phase angle | PC 3.x |
| 43164 | Utility L1L2 Voltage% | Read Only | Multiplier : 0.01 Offset: 0 Size (bits): 16 Sign: U Units: % Lower Limit: NA Upper Limit: NA Default: NA | Utility L1L2 voltage% | PC 3.x |
| 43165 | Utility L1N Voltage% | Read Only | Multiplier : 0.01 Offset: 0 Size (bits): 16 Sign: U Units: % Lower Limit: NA Upper Limit: NA Default: NA | Utility L1N voltage% | PC 3.X |
| 43176 | Utility L2 Power Factor | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 8 Sign: S Unit: PF Lower Limit: Upper Limit: | Utility L2 power factor | PC 3.x |
| 43177 | Utility L2L3 Phase Difference | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: U Unit: Degrees Lower Limit: Upper Limit: | Utility L2L3 voltage phase angle | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43178 | Utility L2L3 Voltage% | Read Only | Multiplier : 0.01 Offset: 0 Size (bits): 16 Sign: U Unit: % Lower Limit: NA Upper Limit: NA | Utility L2L3 voltage% | PC 3.x |
| 43179 | Utility L2N Voltage% | Read Only | Multiplier : 0.01 Offset: 0 Size (bits): 16 Sign: U Unit: % Lower Limit: NA Upper Limit: NA Default: NA | Utility L2N voltage% | PC 3.x |
| 43190 | Utility L3 Power Factor | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 8 Sign: S Unit: PF Lower Limit: NA Upper Limit: NA | Utility L3 power factor | PC 3.x |
| 43191 | Utility L3L1 Phase Difference | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: U Unit: Degrees Lower Limit: NA Upper Limit: NA | Utility L3L1 voltage phase angle | PC 3.x |
| 43192 | Utility L3L1 Voltage% | Read Only | Multiplier : 0.01 Offset: 0 Size (bits): 16 Sign: U Units: % Lower Limit: NA Upper Limit: NA Default: NA | Utility L3L1 voltage% | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43193 | Utility L3N Voltage% | Read Only | Multiplier : 0.01 Offset: 0 Size (bits): 16 Sign: U Units: % Lower Limit: NA Upper Limit: NA Default: NA | Utility L3N voltage% | PC 3.x |
| 43194 | Utility Total kVAh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: kVAh Lower Limit: Upper Limit: | Utility total kVAh accumulation | PC 3.x |
| 43195 | Utility Total kVAh | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: kVAh Lower Limit: Upper Limit: | Utility total kVAh accumulation | PC 3.x |
| 43196 | Exhaust Stack Temperature Right Bank | Read Only | Multiplier : 0.1 Offset: 0 Size (bits): 16 Sign: S Units: degF Lower Limit: -459 Upper Limit: 3155 Default: NA | Monitor point for the Exhaust Stack Temperature Right Bank received from ECM | PC 3.x |
| 43197 | Exhaust Stack Temperature Left Bank | Read Only | Multiplier : 0.1 Offset: 0 Size (bits): 16 Sign: S Units: degF Lower Limit: -459 Upper Limit: 3155 Default: NA | Monitor point for the Exhaust Stack Temperature Left Bank received from ECM | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43200 | Genset Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: -459 Upper Limit: 3155 | Number identifying the model of this generator set. Modbus uses addresses 43200-43219 for the 20 characters of this string. | PC 2.x, PC 3.x |
| 43201 | Genset Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number indentifying the model of this generator set. Modbus uses addresses 43200-43219 for the 20 characters of this string. | PC 2.x, PC 3.x |
| 43202 | Genset Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number identifying the model of this generator set. Modbus uses addresses 43200-43219 for the 20 characters of this string. | PC 2.x, PC 3.x |
| 43203 | Genset Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number identifying the model of this generator set. Modbus uses addresses 43200-43219 for the 20 characters of this string. | PC 2.x, PC 3.x |
| 43204 | Genset Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number identifying the model of this generator set. Modbus uses addresses 43200-43219 for the 20 characters of this string. | PC 2.x, PC 3.x |
| 43205 | Genset Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number identifying the model of this generator set. Modbus uses addresses 43200-43219 for the 20 characters of this string. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43206 | Genset Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number identifying the model of this generator set. Modbus uses addresses 43200-43219 for the 20 characters of this string. | PC 2.x, PC 3.x |
| 43207 | Genset Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number identifying the model of this generator set. Modbus uses addresses 43200-43219 for the 20 characters of this string. | PC 2.x, PC 3.x |
| 43208 | Genset Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number indentifying the model of this generator set. Modbus uses addresses 43200-43219 for the 20 characters of this string. | PC 2.x, PC 3.x |
| 43209 | Genset Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number indentifying the model of this generator set. Modbus uses addresses 43200 - 43219 for the 20 characters of this string. | PC 2.x, PC 3.x |
| 43210 | Genset Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number identifying the model of this generator set. Modbus uses addresses 43200-43219 for the 20 characters of this string. | PC 2.x, PC 3.x |
| 43211 | Genset Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number indentifying the model of this generator set. Modbus uses addresses 43200-43219 for the 20 characters of this string. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43212 | Genset Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number identifying the model of this generator set. Modbus uses addresses 43200-43219 for the 20 characters of this string. | PC 2.x, PC 3.x |
| 43213 | Genset Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number identifying the model of this generator set. Modbus uses addresses 43200-43219 for the 20 characters of this string. | PC 2.x, PC 3.x |
| 43214 | Genset Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number identifying the model of this generator set. Modbus uses addresses 43200-43219 for the 20 characters of this string. | PC 2.x, PC 3.x |
| 43215 | Genset Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number identifying the model of this generator set. Modbus uses addresses 43200-43219 for the 20 characters of this string. | PC 2.x, PC 3.x |
| 43216 | Genset Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number identifying the model of this generator set. Modbus uses addresses 43200-43219 for the 20 characters of this string. | PC 2.x, PC 3.x |
| 43217 | Genset Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number identifying the model of this generator set. Modbus uses addresses 43200-43219 for the 20 characters of this string. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43218 | Genset Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number indentifying the model of this generator set. Modbus uses addresses 43200-43219 for the 20 characters of this string. | PC 2.x, PC 3.x |
| 43219 | Genset Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number identifying the model of this generator set. Modbus uses addresses 43200-43219 for the 20 characters of this string. | PC 2.x, PC 3.x |
| 43220 | Genset Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Serial number of identifying this generator set. Modbus uses addresses 43220-43239 for the 20 characters of this string. | PC 2.x, PC 3.x |
| 43221 | Genset Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Serial number of identifying this generator set. Modbus uses addresses 43220-43239 for the 20 characters of this string. | PC 2.x, PC 3.x |
| 43222 | Genset Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Serial number of identifying this generator set. Modbus uses addresses 43220-43239 for the 20 characters of this string. Uses logical addresses 2048 - 6063 to store the first 16 characters. The last 4 are stored in 691-694. | PC 2.x, PC 3.x |
| 43223 | Genset Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Serial number of identifying this generator set. Modbus uses addresses 43220-43239 for the 20 characters of this string. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43224 | Genset Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Serial number of identifying this generator set. Modbus uses addresses 43220-43239 for the 20 characters of this string. | PC 2.x, PC 3.x |
| 43225 | Genset Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Serial number of identifying this generator set. Modbus uses addresses 43220-43239 for the 20 characters of this string. | PC 2.x, PC 3.x |
| 43226 | Genset Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Serial number of identifying this generator set. Modbus uses addresses 43220-43239 for the 20 characters of this string. | PC 2.x, PC 3.x |
| 43227 | Genset Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Serial number of identifying this generator set. Modbus uses addresses 43220-43239 for the 20 characters of this string. | PC 2.x, PC 3.x |
| 43228 | Genset Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Serial number of identifying this generator set. Modbus uses addresses 43220-43239 for the 20 characters of this string. | PC 2.x, PC 3.x |
| 43229 | Genset Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Serial number of identifying this generator set. Modbus uses addresses 43220-43239 for the 20 characters of this string. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43230 | Genset Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Serial number of identifying this generator set. Modbus uses addresses 43220-43239 for the 20 characters of this string. | PC 2.x, PC 3.x |
| 43231 | Genset Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Serial number of identifying this generator set. Modbus uses addresses 43220-43239 for the 20 characters of this string. | PC 2.x, PC 3.x |
| 43232 | Genset Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Serial number of identifying this generator set. Modbus uses addresses 43220-43239 for the 20 characters of this string. | PC 2.x, PC 3.x |
| 43233 | Genset Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Serial number of identifying this generator set. Modbus uses addresses 43220-43239 for the 20 characters of this string. | PC 2.x, PC 3.x |
| 43234 | Genset Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Serial number of identifying this generator set. Modbus uses addresses 43220-43239 for the 20 characters of this string. | PC 2.x, PC 3.x |
| 43235 | Genset Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Serial number of identifying this generator set. Modbus uses addresses 43220-43239 for the 20 characters of this string. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43236 | Genset Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Serial number of identifying this generator set. Modbus uses addresses 43220-43239 for the 20 characters of this string. | PC 2.x, PC 3.x |
| 43237 | Genset Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Serial number of identifying this generator set. Modbus uses addresses 43220-43239 for the 20 characters of this string. | PC 2.x, PC 3.x |
| 43238 | Genset Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Serial number of identifying this generator set. Modbus uses addresses 43220-43239 for the 20 characters of this string. | PC 2.x, PC 3.x |
| 43239 | Genset Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Serial number of identifying this generator set. Modbus uses addresses 43220-43239 for the 20 characters of this string. | PC 2.x, PC 3.x |
| 43240 | Alternator Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number identifying this generator sets alternator model number. Modbus uses addresses 43240-43259 for the 20 characters text string. | PC 2.x, PC 3.x |
| 43241 | Alternator Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number identifying this generator sets alternator model number. Modbus uses addresses 43240-43259 for the 20 characters text string. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43242 | Alternator Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number identifying this generator sets alternator model number. Modbus uses addresses 43240-43259 for the 20 characters text string. | PC 2.x, PC 3.x |
| 43243 | Alternator Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number identifying this generator sets alternator model number. Modbus uses addresses 43240-43259 for the 20 characters text string. | PC 2.x, PC 3.x |
| 43244 | Alternator Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number identifying this generator sets alternator model number. Modbus uses addresses 43240-43259 for the 20 characters text string. | PC 2.x, PC 3.x |
| 43245 | Alternator Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number identifying this generator sets alternator model number. Modbus uses addresses 43240-43259 for the 20 characters text string. | PC 2.x, PC 3.x |
| 43246 | Alternator Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number identifying this generator sets alternator model number. Modbus uses addresses 43240-43259 for the 20 characters text string. | PC 2.x, PC 3.x |
| 43247 | Alternator Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number identifying this generator sets alternator model number. Modbus uses addresses 43240-43259 for the 20 characters text string. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43248 | Alternator Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number identifying this generator sets alternator model number. Modbus uses addresses 43240-43259 for the 20 characters text string. | PC 2.x, PC 3.x |
| 43249 | Alternator Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number identifying this generator sets alternator model number. Modbus uses addresses 43240-43259 for the 20 characters text string. | PC 2.x, PC 3.x |
| 43250 | Alternator Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number identifying this generator sets alternator model number. Modbus uses addresses 43240-43259 for the 20 characters text string. | PC 2.x, PC 3.x |
| 43251 | Alternator Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number identifying this generator sets alternator model number. Modbus uses addresses 43240-43259 for the 20 characters text string. | PC 2.x, PC 3.x |
| 43252 | Alternator Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number identifying this generator sets alternator model number. Modbus uses addresses 43240-43259 for the 20 characters text string. | PC 2.x, PC 3.x |
| 43253 | Alternator Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number identifying this generator sets alternator model number. Modbus uses addresses 43240-43259 for the 20 characters text string. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43254 | Alternator Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number identifying this generator sets alternator model number. Modbus uses addresses 43240-43259 for the 20 characters text string. | PC 2.x, PC 3.x |
| 43255 | Alternator Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number identifying this generator sets alternator model number. Modbus uses addresses 43240-43259 for the 20 characters text string. | PC 2.x, PC 3.x |
| 43256 | Alternator Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number identifying this generator sets alternator model number. Modbus uses addresses 43240-43259 for the 20 characters text string. | PC 2.x, PC 3.x |
| 43257 | Alternator Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number identifying this generator sets alternator model number. Modbus uses addresses 43240-43259 for the 20 characters text string. | PC 2.x, PC 3.x |
| 43258 | Alternator Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number identifying this generator sets alternator model number. Modbus uses addresses 43240-43259 for the 20 characters text string. | PC 2.x, PC 3.x |
| 43259 | Alternator Model Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Number identifying this generator sets alternator model number. Modbus uses addresses 43240-43259 for the 20 characters text string. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43260 | Alternator Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Unique number identifying this generator sets alternator serial number. Modbus uses addresses 43260-43279 for the 20 characters text string. | PC 2.x, PC 3.x |
| 43261 | Alternator Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Unique number identifying this generator sets alternator serial number. Modbus uses addresses 43260-43279 for the 20 characters text string. | PC 2.x, PC 3.x |
| 43262 | Alternator Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Unique number identifying this generator sets alternator serial number. Modbus uses addresses 43260-43279 for the 20 characters text string. | PC 2.x, PC 3.x |
| 43263 | Alternator Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Unique number identifying this generator sets alternator serial number. Modbus uses addresses 43260-43279 for the 20 characters text string. | PC 2.x, PC 3.x |
| 43264 | Alternator Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Unique number identifying this generator sets alternator serial number. Modbus uses addresses 43260-43279 for the 20 characters text string. | PC 2.x, PC 3.x |
| 43265 | Alternator Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Unique number identifying this generator sets alternator serial number. Modbus uses addresses 43260-43279 for the 20 characters text string. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43266 | Alternator Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Unique number identifying this generator sets alternator serial number. Modbus uses addresses 43260-43279 for the 20 characters text string. | PC 2.x, PC 3.x |
| 43267 | Alternator Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Unique number identifying this generator sets alternator serial number. Modbus uses addresses 43260-43279 for the 20 characters text string. | PC 2.x, PC 3.x |
| 43268 | Alternator Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Unique number identifying this generator sets alternator serial number. Modbus uses addresses 43260-43279 for the 20 characters text string. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43269 | Alternator Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Unique number identifying this generator sets alternator serial number. Modbus uses addresses 43260-43279 for the 20 characters text string. | PC 2.x, PC 3.x |
| 43270 | Alternator Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Unique number identifying this generator sets alternator serial number. Modbus uses addresses 43260-43279 for the 20 characters text string. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43271 | Alternator Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Unique number identifying this generator sets alternator serial number. Modbus uses addresses 43260-43279 for the 20 characters text string. | PC 2.x, PC 3.x |
| 43272 | Alternator Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Unique number identifying this generator sets alternator serial number. Modbus uses addresses 43260-43279 for the 20 characters text string. | PC 2.x, PC 3.x |
| 43273 | Alternator Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Unique number identifying this generator sets alternator serial number. Modbus uses addresses 43260-43279 for the 20 characters text string. | PC 2.x, PC 3.x |
| 43274 | Alternator Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Unique number identifying this generator sets alternator serial number. Modbus uses addresses 43260-43279 for the 20 characters text string. | PC 2.x, PC 3.x |
| 43275 | Alternator Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Unique number identifying this generator sets alternator serial number. Modbus uses addresses 43260-43279 for the 20 characters text string. | PC 2.x, PC 3.x |
| 43276 | Alternator Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Unique number identifying this generator sets alternator serial number. Modbus uses addresses 43260-43279 for the 20 characters text string. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43277 | Alternator Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Unique number identifying this generator sets alternator serial number. Modbus uses addresses 43260-43279 for the 20 characters text string. | PC 2.x, PC 3.x |
| 43278 | Alternator Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Unique number identifying this generator sets alternator serial number. Modbus uses addresses 43260-43279 for the 20 characters text string. | PC 2.x, PC 3.x |
| 43279 | Alternator Serial Number | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Unique number identifying this generator sets alternator serial number. Modbus uses addresses 43260-43279 for the 20 characters text string. | PC 2.x, PC 3.x |
| 43280 | Coolant Level Switch | Read Only | 0: Inactive 1: Active | Coolant Level input software state status. Gives software Inactive/Active state | PC 2.x, PC 3.x |
| 43281 | Coolant Level/Configu rable Input #5 Switch | Read Only | 0: Inactive 1: Active | This is the status of the Configurable Input #5. | PC 2.x, PC 3.x |
| 43283 | Fault Reset Switch | Read Only | 0: Inactive 1: Active | Fault Reset input software state status. Gives software Inactive/Active state | PC 2.x, PC 3.x |
| 43284 | Fault Reset/Config urable Input #10 Switch | Read Only | 0: Inactive 1: Active | This is the status of the Configurable Input #10. | PC 2.x, PC 3.x |
| 43285 | Genset CB Inhibit/Config urable Input #28 Switch | Read Only | 0: Inactive 1: Active | This is the status of the Configurable Input #28. | PC 3.x |
| 43286 | Genset CB Pos B/Configurabl e Input #26 Switch | Read Only | 0: Inactive 1: Active | This is the status of the Configurable Input #26. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43287 | Genset CB Tripped/Confi gurable Input #27 Switch | Read Only | 0: Inactive 1: Active | This is the status of the Configurable Input #27. | PC 3.x |
| 43288 | Genset CB Inhibit Switch | Read Only | 0: Inactive 1: Active | Genset CB Inhibit input software state status. Gives software Inactive/Active state | PC 3.x |
| 43289 | Genset CB Pos A Switch | Read Only | 0: Inactive 1: Active | Genset CB Pos A input software state status. Gives software Inactive/Active state | PC 3.x |
| 43290 | Genset CB Pos B Switch | Read Only | 0: Inactive 1: Active | Genset CB Pos B input software state status. Gives software Inactive/Active state | PC 3.x |
| 43291 | Genset CB Tripped Switch | Read Only | 0: Inactive 1: Active | Genset CB Tripped input software state status. Gives software Inactive/Active state | PC 3.x |
| 43292 | Ground Fault Switch | Read Only | 0: Inactive 1: Active | Ground Fault Switch function output status. Gives software Inactive/Active state | PC 2.x, PC 3.x |
| 43293 | High Alt Temp Switch | Read Only | 0: Inactive 1: Active | High Alt Temperature Switch function output status. Gives software Inactive/Active state | PC 2.x, PC 3.x |
| 43295 | Load Demand Stop/Configur able Input #31 Switch | Read Only | 0: Inactive 1: Active | This is the status of the Configurable Input #31. | PC 3.x |
| 43296 | Local E-stop Switch | Read Only | 0: Inactive 1: Active | Monitors the E–Stop switch. | PC 2.x, PC 3.x |
| 43297 | Low Coolant #2 Switch | Read Only | 0: Inactive 1: Active | Low Coolant #2 Switch function output status. Gives software Inactive/Active state | PC 2.x, PC 3.x |
| 43298 | Low Engine Temperature Switch | Read Only | 0: Inactive 1: Active | Low Engine Temperature Switch function output status. Gives software Inactive/Active state | PC 2.x, PC 3.x |
| 43299 | Low Fuel In Day Tank Switch | Read Only | 0: Inactive 1: Active | Low Fuel In Day Tank Switch function output status. Gives software Inactive/Active state | PC 2.x, PC 3.x |
| 43300 | Genset Bus Delta/Wye Connection | Read/Write | 0: Delta 1: Wye | Delta or Wye for Utility connection | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43301 | Genset Bus Nominal Voltage | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: 110 Upper Limit: 45000 | Generator set Bus nominal voltage | PC 3.x |
| 43302 | Genset Delta/Wye Connection | Read Only | 0: Delta 1: Wye | Delta or Wye for Generator set connection | PC 2.x, PC 3.x |
| 43303 | Genset Nominal Voltage | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: 110 Upper Limit: 45000 | Generator set nominal line- line voltage | PC 2.x, PC 3.x |
| 43304 | Single/3 Phase Connection | Read Only | 0: Single Phase 1: Three Phase | Setup mode interlocked. Generator set’s single phase/3 phase metering setup configuration. | PC 2.x, PC 3.x |
| 43306 | Utility Delta/Wye Connection | Read/Write | 0: Delta 1: Wye | Delta or Wye for Utility connection | PC 3.x |
| 43307 | Utility Nominal Voltage | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: 110 Upper Limit: 45000 | Utility nominal voltage | PC 3.x |
| 43309 | Overfrequenc y Enable | Read/Write | 0: Disabled 1: Enabled | Enables over frequency diagnostic witness test. | PC 2.x, PC 3.x |
| 43310 | Overload Warning Set Time | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 8 Sign: U Unit: seconds Lower Limit: 1 Upper Limit: 120 | The time delay until an overload condition is reported as a fault | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43311 | Overload Warning Threshold | Read/Write | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: U Unit: % Lower Limit: 80 Upper Limit: 140 | Sets the Overload Warning fault trip threshold as percentage of generator set application kW rating. | PC 2.x, PC 3.x |
| 43312 | Overload Shutdown Set Time | Read / Write | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: Seconds Lower Limit: 1 Upper Limit: 120 Default: 60 | The time delay until an overload condition is reported as Shutdown fault | PC 3.x |
| 43313 | Overload Shutdown threshold | Read / Write | Multiplier : 0.01 Offset: 0 Size (bits): 16 Sign: U Units: % Lower Limit: 70 Upper Limit: 655.35 Default: 655.35 | Sets the Overload Shutdown fault trip threshold as percentage of genset application kW rating. To disable the Overload shutdown fault set the value to 655.35 or Not Available. | PC 3.x |
| 43314 | Prelube Function Owner | Read / Write | 0: GCS 1: ECS | Selects whether prelube function is being controlled by GCS or ECS | PC 3.x |
| 43315 | Non Lubricated Non- Emergency Start | Read / Write | 0: Allow Start 1: Block Start | Selects whether to allow or block genset starting when not lubricated in case of Non- Emergency start. Applicable only when Prelube Function Owner = ECS | PC 3.x |
| 43338 | CAN Failure Retries | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 8 Sign: U Unit: Lower Limit: 0 Upper Limit: 10 | Sets the maximum number of CAN communication retries | PC 2.x, PC 3.x |
| 43339 | Auto Sleep Enable | Read/Write | 0: Awake in Auto 1: Sleep in Auto | Trim that determines if the control will stay awake in Auto mode or Fall asleep in Auto mode. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43340 | Max Setup Mode Time | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Seconds Lower Limit: 30 Upper Limit: 3600 | Max time allowed in Setup Mode. | PC 2.x, PC 3.x |
| 43341 | Power Down Mode Enable | Read/Write | 0: Disable 1: Enable | Trim to enable Sleep Mode | PC 2.x, PC 3.x |
| 43342 | Power Down Mode Time Delay | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Seconds Lower Limit: 0 Upper Limit: 600 | Timer setting for the Power Down delay feature | PC 2.x, PC 3.x |
| 43343 | Setup Mode Enable | Read/Write | 0: Disable 1: Enable | Volatile to allow entry into Setup Mode | PC 2.x, PC 3.x |
| 43344 | Clock Date | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 8 Sign: U Unit: Lower Limit: 1 Upper Limit: 31 | Use to set or read the current date. | PC 2.x, PC 3.x |
| 43345 | Clock Hour | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 8 Sign: U Unit: Lower Limit: 1 Upper Limit: 32 | Use to set or read the current hour. | PC 2.x, PC 3.x |
| 43346 | Clock Minute | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 8 Sign: U Unit: Lower Limit: 0 Upper Limit: 59 | Use to set or read the current minute. | PC 2.x, PC 3.x |
| 43347 | Clock Mode | Read/Write | 0: Normal 1: Set Clock 2: Save Clock | Use to set the real time clock and save settings. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43348 | Clock Month | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 8 Sign: U Unit: Lower Limit: 1 Upper Limit: 12 | Use to set or read the current month. | PC 2.x, PC 3.x |
| 43349 | Clock Second | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 8 Sign: U Unit: Lower Limit: 0 Upper Limit: 59 | Use to set or read the current second. | PC 2.x, PC 3.x |
| 43350 | Clock Year | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 8 Sign: U Unit: Lower Limit: 0 Upper Limit: 99 | Use to set or read the current year. | PC 2.x, PC 3.x |
| 43351 | Daylight Savings End Hour | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 8 Sign: U Unit: Lower Limit: 2 Upper Limit: 19 | Use to set the hour of the day when daylight savings time ends. | PC 2.x, PC 3.x |
| 43352 | Daylight Savings End Month | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 8 Sign: U Unit: Lower Limit: 1 Upper Limit: 12 | Use to set the month when daylight savings time ends. | PC 2.x, PC 3.x |
| 43353 | Daylight Savings End Week Occurrence in Month | Read/Write | 0: First Occurrence 1: Second Occurrence 2: Third Occurrence 3: Fourth Occurrence 4: Last Occurrence | Use to set the week of the month when daylight savings time ends. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43354 | Daylight Savings Start Day | Read/Write | 0: Sunday 1: Monday 2: Tuesday 3: Wednesday 4: Thursday 5: Friday 6: Saturday | Use to set the day of the week when daylight savings time starts. | PC 2.x, PC 3.x |
| 43355 | Daylight Savings Start Hour | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 8 Sign: U Unit: Lower Limit: 2 Upper Limit: 19 | Use to set the hour of the day when daylight savings time starts. | PC 2.x, PC 3.x |
| 43356 | Daylight Savings Start Month | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 8 Sign: U Unit: Lower Limit: 1 Upper Limit: 12 | Use to set the month when daylight savings time starts. | PC 2.x, PC 3.x |
| 43357 | Daylight Savings Start Week Occurrence in Month | Read/Write | 0: First Occurrence 1: Second Occurrence 2: Third Occurrence 3: Fourth Occurrence 4: Last Occurrence | Use to set the week of the month when daylight savings time starts. | PC 2.x, PC 3.x |
| 43358 | Daylight Savings Time Adjustment | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 8 Sign: U Unit: Minutes Lower Limit: 0 Upper Limit: 120 | Use to set the amount of daylight savings time adjustment applied. | PC 2.x, PC 3.x |
| 43359 | Daylight Savings Time Enable | Read/Write | 0: Disabled 1: Enabled | Use to enable the daylight savings time feature. | PC 2.x, PC 3.x |
| 43360 | Exercise Scheduler Enable | Read/Write | 0: Disabled 1: Enabled | Enables the exercise scheduler. | PC 2.x, PC 3.x |
| 43361 | Reset Fuel Consumption | Read/Write | 0: Inactive 1: Active | The reset trip fuel consumption command. | PC 2.x, PC 3.x |
| 43362 | Reset Runs | Read/Write | 0: Inactive 1: Active | The reset runs command. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43363 | Reset Start Attempts | Read/Write | 0: Inactive 1: Active | The reset start attempts command. | PC 2.x, PC 3.x |
| 43364 | Scheduler Exception Select | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 8 Sign: U Unit: Lower Limit: 1 Upper Limit: 6 | Used to select an exception to adjust. | PC 2.x, PC 3.x |
| 43365 | Scheduler Exception x Date | Read / Write | Multiplier : 1 Offset: 0 Size (bits): 8 Sign: U Units: NA Lower Limit: 1 Upper Limit: 31 | Used to adjust the date for the selected exception. | PC 2.x, PC 3.x |
| 43366 | Scheduler Exception x Duration Days | Read / Write | Multiplier : 1 Offset: 0 Size (bits): 8 Sign: U Units: NA Lower Limit: 0 Upper Limit: 44 | Used to adjust the length in days for the selected exception. | PC 2.x, PC 3.x |
| 43367 | Scheduler Exception x Duration Hours | Read / Write | Multiplier : 1 Offset: 0 Size (bits): 8 Sign: U Units: NA Lower Limit: 0 Upper Limit: 23 | Used to adjust the length in hours for the selected exception. | PC 2.x, PC 3.x |
| 43368 | Scheduler Exception x Duration Minutes | Read / Write | Multiplier : 1 Offset: 0 Size (bits): 8 Sign: U Units: NA Lower Limit: 0 Upper Limit: 59 Default: 0 | Used to adjust the length in minutes for the selected exception. | PC 2.x, PC 3.x |
| 43369 | Scheduler Exception x Enable | Read / Write | - : Disable - : Enable | Used to enable or disable the selected exception. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43370 | Scheduler Exception x Hour | Read / Write | Multiplier : 1 Offset: 0 Size (bits): 8 Sign: U Units: NA Lower Limit: 0 Upper Limit: 23 Default: 0 | Used to adjust the starting hour for the selected exception. | PC 2.x PC 3.x |
| 43371 | Scheduler Exception x Minute | Read / Write | Multiplier : 1 Offset: 0 Size (bits): 8 Sign: U Units: NA Lower Limit: 0 Upper Limit: 59 Default: 0 | Used to adjust the starting minute for the selected exception. | PC 2.x, PC 3.x |
| 43372 | Scheduler Exception x Month | Read / Write | Multiplier : 1 Offset: 0 Size (bits): 8 Sign: U Units: NA Lower Limit: 1 Upper Limit: 12 Default: 1 | Used to adjust the starting month for the selected exception. | PC 2.x, PC 3.x |
| 43373 | Scheduler Exception x Repeat | Read / Write | 0: Once Only 1: Every Year | Used to adjust the repeat interval for the selected exception. | PC 2.x, PC 3.x |
| 43374 | Scheduler Program Select | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 8 Sign: U Unit: Lower Limit: 1 Upper Limit: 12 | Used to select a program to adjust. | PC 2.x, PC 3.x |
| 43375 | Scheduler Program x Duration Hours | Read / Write | Multiplier : 1 Offset: 0 Size (bits): 8 Sign: U Units: NA Lower Limit: 0 Upper Limit: 23 Default: 0 | Used to adjust the length in hours for the selected program. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43376 | Scheduler Program x Duration Minutes | Read / Write | Multiplier : 1 Offset: 0 Size (bits): 8 Sign: U Units: NA Lower Limit: 0 Upper Limit: 59 Default: 0 | Used to adjust the length in minutes for the selected program. | PC 2.x, PC 3.x |
| 43377 | Scheduler Program x Enable | Read/Write | 0: Disable 1: Enable | Used to enable or disable the selected program. | PC 2.x, PC 3.x |
| 43378 | Scheduler Program x Repeat Interval | Read / Write | 0: Once 1: Every Week 2: Every 2 Weeks 3: Every 3 Weeks 4: Every 4 Weeks 5: Every 5 Weeks 6: First Week of Month 7: Second Week of Month 8: Third Week of Month 9: Fourth Week of Month 10: Last Week of Month | Used to adjust the repeat interval for the selected program. | PC 2.x, PC 3.x |
| 43379 | Scheduler Program x Run Mode | Read/Write | 0: No Load 1: With Load 2: Extended Parallel | Used to adjust the run mode for the selected program. | PC 3.x |
| 43380 | Scheduler Program x Start Day | Read / Write | 0: Sunday 1: Monday 2: Tuesday 3: Wednesday 4: Thursday 5: Friday 6: Saturday | Used to adjust the start day of the week for the selected program. | PC 2.x, PC 3.x |
| 43381 | Scheduler Program x Start Hour | Read / Write | Multiplier : 1 Offset: 0 Size (bits): 8 Sign: U Units: NA Lower Limit: 0 Upper Limit: 23 Default: 0 | Used to adjust the start hour for the selected program. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43382 | Scheduler Program x Start Minute | Read / Write | Multiplier : 1 Offset: 0 Size (bits): 8 Sign: U Units: NA Lower Limit: 0 Upper Limit: 59 Default: 0 | Used to adjust the start minute for the selected program. | PC 2.x, PC 3.x |
| 43383 | Daylight Savings End Day | Read/Write | 0: Sunday 1: Monday 2: Tuesday 3: Wednesday 4: Thursday 5: Friday 6: Saturday | Use to set the day of the week when daylight savings time ends. | PC 2.x, PC 3.x |
| 43501 | Genset Run Type | Read Only | 0: Emergency Remote Start 1: Non Emergency Remote Start 2: Load Demand Start 3: Manual Run 4: Exercise | Source or type of current genset run (if running) or previous genset run (if stopped). | PC 2.x, PC 3.x |
| 43502 | Idle Rated Command | Read Only | 0: Idle 1: Rated | The output command of the Idle/Rated Logic | PC 2.x, PC 3.x |
| 43503 | Idle Request | Read Only | 0: False 1: True | Indicates a request to go to manual idle. Manual idle allowed if breaker is open or not controlled | PC 2.x, PC 3.x |
| 43506 | Load Dump Command | Read Only | 0: Inactive 1: Active 2: Reserved 3: Not Available | Monitors the software command to the load dump driver output | PC 2.x, PC 3.x |
| 43507 | Load Dump Overload Condition | Read Only | 0: Inactive 1: Active 2: Reserved 3: Not Available | Monitors the state of the load dump overload detection algorithm | PC 2.x, PC 3.x |
| 43508 | Load Dump Underfrequen cy Condition | Read Only | 0: Inactive 1: Active 2: Reserved 3: Not Available | The state of the load dump underfrequency detection algorithm | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43509 | Low Battery Voltage Running Threshold | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Vdc Lower Limit: Upper Limit: | The low battery voltage threshold when the generator set is in rated mode | PC 2.x, PC 3.x |
| 43510 | Low Battery Voltage Stopped Threshold | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Vdc Lower Limit: Upper Limit: | The low battery voltage threshold when the generator set is not in rated mode | PC 2.x, PC 3.x |
| 43511 | Low Battery Voltage Threshold | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Vdc Lower Limit: Upper Limit: | The selection of the running or stopped threshold | PC 2.x, PC 3.x |
| 43512 | Manual Command | Read Only | 0: Not Manual 1: Manual | The output of the Manual Command OR logic | PC 2.x, PC 3.x |
| 43513 | Manual Command Inputs | Read Only | Multiplier : 1 Offset: 0 Size (bits): 8 Sign: U Units: NA Lower Limit: NA Upper Limit: NA Default: NA | Bitmask to show the inputs to the Command output which are currently on | PC 2.x, PC 3.x |
| 43515 | Oil Priming Pump Command | Read Only | 0: Inactive 1: Active 2: Reserved 3: Not Available | The Prelube Driver Command. | PC 2.x, PC 3.x |
| 43516 | Prelube Mode | Read Only | 0: Crank After Prelube 1: Crank With Prelube 2: Prelube Only | Set to a required mode based on the type of starting requirement | PC 2.x, PC 3.x |
| 43517 | Prelube State | Read Only | 0: Complete 1: Armed 2: Prelube Output ON 3: Prelube Output OFF 4: Enable Crank | The monitor point for the prelube state. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43518 | PTC Genset Operating Mode | Read Only | 0: Off 1: Manual 2: Normal 3: Normal Override 4: Test 5: Exercise 6: Utility Fail 7: Extended Parallel | Current mode for the genset operation part of the PTC function | PC 3.x |
| 43519 | PTC Mode Switch Command | Read Only | 0: Inactive 1: Active 2: Reserved 3: Not Available | The output of the PTC Mode Switch Command OR logic | PC 3.x |
| 43520 | PTC Mode Switch Command Inputs | Read Only | Multiplier : 1 Offset: 0 Size (bits): 8 Sign: U Units: NA Lower Limit: NA Upper Limit: NA Default: NA | Bitmask to show the inputs to the Command output which are currently on. | PC 3.x |
| 43521 | PTC Status | Read Only | 0: Off/ Not Enabled 1: Manual Mode 2: Normal Utility 3: Retransfer 4: Retransfer Override 5: Emergency Test 6: Normal Test 7: Exercise 8: Utility Failure 9: Extended Parallel | Indicates what the current state is of PTC control action | PC 3.x |
| 43522 | PTC Transfer Pair Operating Mode | Read Only | 0: Off 1: Manual 2: Normal 3: Normal Override 4: Test 5: Exercise 6: Utility Fail 7: Extended Parallel | Operation mode for the breaker pair portion of the PTC function | PC 3.x |
| 43523 | Ready to Load Command | Read Only | 0: Inactive 1: Active 2: Reserved 3: Not Available | The state that the Ready to Load Driver output is being commanded to | PC 2.x, PC 3.x |
| 43524 | Remote Start Command | Read Only | 0: Stop 1: Start | The output of the Remote Start Command OR logic | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43526 | Remote Start State | Read Only | 0: Off 1: Remote Start 2: Load Demand Stop 3: Load Demand Start | Status of remote start and load demand stop inputs | PC 2.x, PC 3.x |
| 43527 | RMS Regulation Error | Read Only | Multiplier : 0.01 Offset: 0 Size (bits): 16 Sign: S Units: % Lower Limit: -100 Upper Limit: 100 Default: NA | The RMS voltage (or current) error at the AVR | PC 2.x, PC 3.x |
| 43528 | Run Command | Read Only | 0: Off 1: Run | The signal that is commanding a change to the run mode | PC 2.x, PC 3.x |
| 43529 | Run Relay Command | Read Only | 0: Inactive 1: Active | The status of relay command when genset is in frequency and rated mode. | PC 2.x, PC 3.x |
| 43530 | Speed and Voltage Bias Relay Command | Read Only | 0: Inactive 1: Active | Monitor point for the command which closes the on-board relay enabling the voltage and speed bias outputs. | PC 3.x |
| 43531 | Speed Bias Command | Read Only | Multiplier : 0.01 Offset: 0 Size (bits): 16 Sign: S Units: % Lower Limit: 0 Upper Limit: NA Default: NA | Indicates amount of speed bias offset GCS is commanding to ECS governor or external governor | PC 3.x |
| 43533 | Start Countdown | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 0 Upper Limit: 300 Default: NA | Time remaining until start is initiated | PC 2.x, PC 3.x |
| 43536 | Start Type Command | Read Only | 0: Emergency 1: Non Emergency | The output of the Start Type Command OR logic | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43537 | Start Type Command Inputs | Read Only | Multiplier : 1 Offset: 0 Size (bits): 8 Sign: U Units: NA Lower Limit: NA Upper Limit: NA Default: NA | Bitmask to show the inputs to the Command output which are currently on | PC 2.x, PC 3.x |
| 43538 | Starter Command | Read Only | 0: Inactive 1: Active 2: Reserved 3: Not Available | State of hardware output. | PC 2.x, PC 3.x |
| 43539 | Stop Countdown | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 0 Upper Limit: 5000 | Time remaining until generator set stops | PC 2.x, PC 3.x |
| 43540 | Switch Panel Run Request | Read Only | 0: None 1: Manual 2: Exercise | Status of run and exercise commands from display panel | PC 2.x, PC 3.x |
| 43542 | Target Voltage | Read Only | Multiplier : 0.01 Offset: 0 Size (bits): 16 Sign: U Units: % Lower Limit: 0 Upper Limit: 150 Default: NA | The target voltage without ramping and torque match voltage rolloff effects | PC 2.x, PC 3.x |
| 43543 | Time At No Load | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 0 Upper Limit: 600 Default: NA | Amount of time the generator set has run at no load | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43544 | Time at Rated Cooldown | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 0 Upper Limit: 5000 | Amount of time spend in Rated Cooldown | PC 2.x, PC 3.x |
| 43546 | Voltage Bias Command | Read Only | Multiplier : 0.01 Offset: 0 Size (bits): 16 Sign: S Units: % Lower Limit: 0 Upper Limit: NA Default: NA | Indicates amount of voltage bias offset GCS is commanding to an external regulator | PC 3.x |
| 43547 | Voltage Setpoint | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: U Units: % Lower Limit: 0 Upper Limit: 150 | The voltage setpoint command | PC 2.x, PC 3.x |
| 43550 | Weak Battery Threshold | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Vdc Lower Limit: 6 Upper Limit: 16 | Monitor point for the weak battery voltage threshold | PC 2.x, PC 3.x |
| 43551 | Weak Battery Voltage Set Time | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 1 Upper Limit: 5 | The time delay until a weak battery condition is reported as a fault | PC 2.x, PC 3.x |
| 43552 | Paralleling Voltage Ref Offset | Read Only | Multiplier : 0.01 Offset: 0 Size (bits): 16 Sign: S Units: % Lower Limit: NA Upper Limit: NA | Voltage offset to voltage regulator for paralleling function | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43553 | Synchronizer Status | Read Only | 0: Synchronizer Off 1: Synchronizer On | Indicates whether synchronizer is on or off | PC 3.x |
| 43554 | Active Transition Timer | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: Upper Limit: | Countdown value of the active transition timer | PC 3.x |
| 43555 | Active Transition Type | Read Only | 0: None 1: Programmed Transition 2: Transfer 3: Retransfer 4: Max Parallel | Indicates the active transition type for PTC | PC 3.x |
| 43556 | Arbitration State | Read Only | 0: Off 1: Arbitrate0 2: Winner 3: Arbitrate1 4: Sleep | Indicates current arbitration state | PC3.x |
| 43557 | Arbitration Timer | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: msec Lower Limit: NA Upper Limit: NA Default: NA | Arbitration loop countdown timer | PC 3.x |
| 43567 | Genset Current Based Breaker Position | Read Only | 0: Unknown 1: Closed | Indicates genset breaker position based on current | PC 3.x |
| 43558 | ES State | Read Only | 0: Standby 1: Dead Bus 2: Synchronize 3: Load Share 4: Load Govern | Internal paralleling status variable | PC 3.x |
| 43559 | First Start State | Read Only | 0: First Start Not Allowed 1: First Start Requested 2: First Start Permitted | Indicates status of the first start system | PC 3.x |
| 43560 | Genset CB Close Command | Read Only | 0: Inactive 1: Active | Generator set cb close command status | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43561 | Genset CB Fail To Close Lockout | Read Only | 0: Inactive 1: Active | Status of gen fail to close lockout function | PC 3.x |
| 43562 | Genset CB Position Status | Read Only | 0: Open 1: Closed 2: Not Available | Indicates generator set breaker position | PC 3.x |
| 43563 | Genset Availability Status | Read Only | 0: Not Available 1: Available 2: Unknown | Indicates status of the generator set source | PC 3.x |
| 43564 | Bus Status | Read Only | 0: Unavailable 1: Dead 2: Live | Indicates status of the bus | PC 3.x |
| 43565 | Genset CB Inhibit Command | Read Only | 0: Inactive 1: Active | Generator set cb inhibit command | PC 3.x |
| 43566 | Genset CB Tripped Command | Read Only | 0: Inactive 1: Active | Generator set cb tripped command | PC 3.x |
| 43568 | Genset Frequency Lower Drop- Out Threshold | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Hz Lower Limit: Upper Limit: | Indicates the lower drop-out threshold in Hz for generator set frequency sensor | PC 3.x |
| 43569 | Genset Frequency Lower Pick- Up Threshold | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Hz Lower Limit: Upper Limit | Indicates the lower pick-up threshold in Hz for generator set frequency sensor | PC 3.x |
| 43570 | Genset Frequency Sensor Status | Read Only | 0: Unknown 1: Picked Up 2: Dropped Out | Indicates generator set frequency sensor status | PC 3.x |
| 43571 | Genset Frequency Upper Drop- Out Threshold | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Hz Lower Limit: Upper Limit | Indicates the upper drop-out threshold in Hz for generator set frequency sensor | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43572 | Genset Frequency Upper Pick- Up Threshold | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Hz Lower Limit: Upper Limit | Indicates the upper pick-up threshold in Hz for generator set frequency sensor | PC 3.x |
| 43573 | Genset Loss of Phase Sensor Status | Read Only | 0: Unknown 1: Picked Up 2: Dropped Out | Indicates generator set loss of phase sensor status | PC 3.x |
| 43574 | Genset Overvoltage Drop-Out Threshold | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit | Indicates the drop-out threshold in volts for generator set over voltage sensor | PC 3.x |
| 43575 | Genset Overvoltage Pick-Up Threshold | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit | Indicates the pick-up threshold in volts for generator set over voltage sensor | PC 3.x |
| 43576 | Genset Overvoltage Sensor Status | Read Only | 0: Unknown 1: Picked Up 2: Dropped Out | Indicates generator set over voltage sensor status | PC 3.x |
| 43577 | Genset Phase Rotation Sensor Status | Read Only | 0: Unknown 1: Picked Up 2: Dropped Out | Indicates generator set phase rotation sensor status | PC 3.x |
| 43578 | Genset Undervoltage Drop-Out Threshold | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit | Indicates the drop-out threshold in volts for generator set under voltage sensor | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43579 | Genset Undervoltage Pick-Up Threshold | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit | Indicates the pick-up threshold in volts for generator set under voltage sensor | PC 3.x |
| 43580 | Genset Undervoltage Sensor Status | Read Only | 0: Unknown 1: Picked Up 2: Dropped Out | Indicates generator set under voltage sensor status | PC 3.x |
| 43581 | Master First Start Output Command | Read Only | 0: Inactive 1: Active | Status of the first start output command | PC 3.x |
| 43582 | Maximum Parallel Timer | Read Only | Multiplier : 0.1 Offset: 0 Size (bits): 16 Sign: U Units: Seconds Lower Limit: NA Upper Limit: NA Default: NA | Countdown value of the maximum parallel timer | PC 3.x |
| 43583 | Maximum Parallel Timer Status | Read Only | 0: Not Timing 1: Timing 2: Expired | Indicates status of the maximum parallel timer | PC 3.x |
| 43584 | Paralleling Speed Control Mode | Read Only | 0: Isochronous 1: Droop 2: Synchronize 3: Load Share 4: Load Govern | Indicates which speed control algorithm is in effect | PC 2.x, PC 3.x |
| 43585 | Paralleling Voltage Control Mode | Read Only | 0: Isochronous 1: Droop 2: Synchronize 3: Load Share 4: Load Govern | Indicates which voltage control algorithm is in effect | PC 2.x, PC 3.x |
| 43586 | Programmed Transition Timer | Read Only | Multiplier : 0.1 Offset: 0 Size (bits): 16 Sign: U Units: Seconds Lower Limit: NA Upper Limit: NA Default: NA | Countdown value of the programmed transition timer | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43587 | Programmed Transition Timer Status | Read Only | 0: Not Timing 1: Timing 2: Expired | Indicates status of the programmed transition timer | PC 3.x |
| 43588 | PTC Enable Status | Read Only | 0: Disable 1: Enable | Indicates if PTC functions are running | PC 3.x |
| 43589 | PTC Operating Transition Type | Read Only | 0: Open Transition 1: Hard Closed Transition 2: Soft Closed Transition | Indicates the transition type currently in effect | PC 3.x |
| 43590 | PTC State | Read Only | 0: PTC Not Enabled 1: No Source Connected 2: Utility Connected 3: Genset Connected 4: Paralleled | Indicates the connected state of the Power Transfer Control | PC 3.x |
| 43591 | Retransfer Timer | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Units: Seconds Lower Limit: NA Upper Limit: NA Default: NA | Countdown value of the retransfer timer | PC 3.x |
| 43592 | Retransfer Timer Status | Read Only | 0: Not Timing 1: Timing 2: Expired | Indicates status of the retransfer timer | PC 3.x |
| 43593 | Speed Droop Enable Command | Read Only | 0: Inactive 1: Active | Command value of speed droop enable | PC 2.x, PC 3.x |
| 43594 | Speed Droop Status | Read Only | 0: Droop Disabled 1: Droop Enabled | Indicates whether or not speed droop is in effect | PC 2.x, PC 3.x |
| 43595 | Transfer Timer | Read Only | Multiplier : 0.1 Offset: 0 Size (bits): 16 Sign: U Units: Seconds Lower Limit: NA Upper Limit: NA Default: NA | Countdown value of the transfer timer | PC3.x |
| 43596 | Transfer Timer Status | Read Only | 0: Not Timing 1: Timing 2: Expired | Indicates status of the transfer timer | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43597 | Utility CB Close Command | Read Only | 0: Inactive 1: Active | Utility cb close command status | PC 3.x |
| 43598 | Utility CB Open Command | Read Only | 0: Inactive 1: Active | Utility cb open command status | PC 3.x |
| 43599 | Utility CB Position Status | Read Only | 0: Open 1: Closed 2: Not Available | Indicates utility breaker position | PC 3.x |
| 43600 | Load Govern kW Method | Read/Write | 0: Genset kW 1: Genset kW w/Utility Constraint 2: Utility kW | Use to select how generator set kW output will be controlled when paralleled to utility. | PC 3.x |
| 43608 | Configurable Output #1 Event Code | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | The event code for this output. | PC 2.x, PC 3.x |
| 43610 | Configurable Output #2 Event Code | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | The event code for this output. | PC 2.x, PC 3.x |
| 43613 | Configurable Output #20 Event Code | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | The event code for this output. | PC 3.x |
| 43616 | Configurable Output #21 Event Code | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | The event code for this output. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43619 | Configurable Output #22 Event Code | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | The event code for this output. | PC 3.x |
| 43622 | Configurable Output #3 Event Code | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | The event code for this output. | PC 2.x, PC 3.x |
| 43625 | Configurable Output #4 Event Code | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | The event code for this output. | PC 2.x, PC 3.x |
| 43641 | Delayed Shutdown Enable | Read/Write | 0: Disabled 1: Enabled | Enables the Delayed Shutdown feature. | PC 2.x, PC 3.x |
| 43642 | Delayed Shutdown Time Delay | Read/Write | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 0 Upper Limit: 3 | Sets the shutdown fault delayed time delay for the Delayed Shutdown feature. | PC 2.x, PC 3.x |
| 43643 | Remote Fault Reset Enabled | Read/Write | 0: Disable 1: Enable | Trim to enable Remote Fault Reset. Can only reset Warning Faults | PC 2.x, PC 3.x |
| 43644 | Fail To Shutdown Delay | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 0 Upper Limit: 30 | Trim to set the time for a shutdown fault to be active and the generator set not shutting down before the Fail to Shutdown fault occurs. | PC 2.x, PC 3.x |
| 43645 | LCL Detection Response | Read/Write | 0: None 1: Warning 2: Shutdown | Sets low coolant level fault response to None, Warning, or Shutdown. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43646 | LCT Warning Clear Time | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 8 Sign: U Unit: Minutes Lower Limit: 0 Upper Limit: 30 | Sets time to clear the low coolant temperature fault. | PC 2.x, PC 3.x |
| 43647 | LCT Warning Set Time | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 8 Sign: U Unit: Minutes Lower Limit: 0 Upper Limit: 30 | Sets time to set the low coolant temperature fault. | PC 2.x, PC 3.x |
| 43648 | LCT Warning Threshold | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: -20 Upper Limit: 100 | Sets threshold for the low coolant temperature fault warning. | PC 2.x, PC 3.x |
| 43649 | V/Hz Knee Frequency | Read/Write | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Hz Lower Limit: 0 Upper Limit: 10 | The voltage will roll off (decrease) proportionally to the V/Hz setup, once the frequency drops below the set point in the V/Hz Knee Frequency. This allows the generator set to recover faster when the frequency drops. | PC 2.x, PC 3.x |
| 43650 | V/Hz Rolloff Slope | Read/Write | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: % / Hz Lower Limit: 0 Upper Limit: 10 | The amount of voltage roll off when the frequency is below the knee frequency | PC 2.x, PC 3.x |
| 43651 | 12 V High Battery Voltage Threshold | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Vdc Lower Limit: 14 Upper Limit: 17 | Sets 12V high battery voltage fault threshold. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43652 | 12 V Low Battery Voltage Running Threshold | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Vdc Lower Limit: 12 Upper Limit: 16 | Sets 12V low battery voltage fault threshold for generator set operation while in rated mode | PC 2.x, PC 3.x |
| 43653 | 12 V Low Battery Voltage Stopped Threshold | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Vdc Lower Limit: 11 Upper Limit: 13 | Sets 12V low battery voltage fault threshold for generator set operation in all modes except rated | PC 2.x, PC 3.x |
| 43654 | 12 V Weak Battery Voltage Threshold | Read/Write | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Vdc Lower Limit: 6 Upper Limit: 10 | Sets 12V weak battery voltage fault threshold | PC 2.x, PC 3.x |
| 43655 | 24 V High Battery Voltage Threshold | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Vdc Lower Limit: 28 Upper Limit: 34 | Sets 24V high battery voltage fault threshold | PC 2.x, PC 3.x |
| 43656 | 24 V Low Battery Voltage Running Threshold | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Vdc Lower Limit: 24 Upper Limit: 28 | Sets 24V low battery voltage fault threshold for generator set operation while in rated mode | PC 2.x, PC 3.x |
| 43657 | 24 V Low Battery Voltage Stopped Threshold | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Vdc Lower Limit: 24 Upper Limit: 26 | Sets 24V low battery voltage fault threshold for generator set operation in all modes except rated | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43658 | 24 V Weak Battery Voltage Threshold | Read/Write | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Vdc Lower Limit: 12 Upper Limit: 16 | Sets 24V weak battery voltage fault threshold | PC 2.x, PC 3.x |
| 43659 | Adjustable Freq/Speed Gain | Read/Write | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: U Unit: RPM/Hz Lower Limit: 12 Upper Limit: 240 | Sets the RPM/Hz conversion factor when the Freq to Speed Gain Select trim is set to this trim | PC 2.x, PC 3.x |
| 43660 | Alternate Frequency Switch | Read Only | 0: 50 Hz 1: 60 Hz | Sets the generator set nominal frequency. | PC 2.x, PC 3.x |
| 43661 | AVR Gain Adjust Trim | Read/Write | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0.05 Upper Limit: 10 | A trim that allows the user to modify the overall gains of the AVR. | PC 2.x, PC 3.x |
| 43662 | Charging Alternator Fault Time Delay | Read/Write | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 2 Upper Limit: 300 | Sets the time delay for the charging alt failure fault | PC 2.x, PC 3.x |
| 43663 | Continuous Crank Engage Time | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 40 Upper Limit: 100 | Sets the maximum amount of time to engage the starter when using the continuous cranking method | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43664 | Controlled Shutdown Advance Notice Delay | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 0 Upper Limit: 300 | Delay allowed for a shutdown with cooldown fault prior to shutting down the generator set | PC 3.x |
| 43665 | Crank Attempts | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 1 Upper Limit: 7 | Sets the maximum number of times to engage the starter when attempting to start engine using the cycle cranking method | PC 2.x, PC 3.x |
| 43666 | Cycle / Cont Crank Select | Read Only | 0: Cycle 1: Continuous | Selects whether to use continuous cranking or cycle cranking when attempting to start engine | PC 2.x, PC 3.x |
| 43667 | Cycle Crank Engage Time | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 2 Upper Limit: 20 | Sets the maximum amount of time to engage the starter during a single crank attempt when using the cycle cranking method | PC 2.x, PC 3.x |
| 43668 | Cycle Crank Rest Time | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 7 Upper Limit: 40 | Sets the amount of time to wait between crank attempts | PC 2.x, PC 3.x |
| 43669 | Delayed Off FSO Relay Time | Read/Write | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 0 Upper Limit: 120 | Time delay between when the Delayed Off Command turns off and Run Command turns off | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43670 | External AVR Knee Frequency | Read / Write | Multiplier : 0.1 Offset: 0 Size (bits): 16 Sign: U Units: Hz Lower Limit: 0 Upper Limit: 10 Default: NA | Sets the knee frequency for the fixed knee freq logic. | PC 2.x, PC 3.x |
| 43671 | External Bias Commands Enable | Read/Write | 0: Disabled 1: Enabled | Enables the external bias (speed and voltage commands) to the hardware outputs. | PC 3.x |
| 43672 | Frequency Adjust | Read/Write | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: S Units: Hz Lower Limit: -6 Upper Limit: 6 | A method of adding in a frequency offset to the base frequency subject to high and low limit calibrations | PC 2.x, PC 3.x |
| 43673 | Genset Exercise Time | Read/Write | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: hours Lower Limit: 0 Upper Limit: 25 | Sets the total exercise time not including warmup at idle or idle cooldown time | PC 2.x, PC 3.x |
| 43674 | Governor Gain Adjust | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0.05 Upper Limit: 15 | A trim that allows the user to modify the overall gain of the governor | PC 2.x, PC 3.x |
| 43675 | High Battery Voltage Set Time | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 2 Upper Limit: 60 | The time delay until a high battery voltage condition is reported as a fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43676 | High Battery Voltage Threshold | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Vdc Lower Limit: Upper Limit: | The high battery voltage threshold | PC 2.x, PC 3.x |
| 43677 | Idle Cooldown Time | Read/Write | Multiplier: 0.25 Offset: 0 Size (bits): 16 Sign: U Unit: minutes Lower Limit: 0 Upper Limit: 60 | Sets time to run at idle before shutting down generator set on normal stops | PC 2.x, PC 3.x |
| 43678 | Idle Speed | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: RPM Lower Limit: 700 Upper Limit: 1100 | Sets the speed at which the engine will idle subject to high and low limit calibrations | PC 2.x, PC 3.x |
| 43679 | Idle to Rated Ramp Time | Read/Write | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 0 Upper Limit: 30 | The time over which the speed reference is to ramp from idle speed to rated speed | PC 2.x, PC 3.x |
| 43680 | Idle Warmup Coolant Temp | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: -40 Upper Limit: 300 | Coolant temperature threshold to end idle warmup time | PC 2.x, PC 3.x |
| 43681 | Idle Warmup Time | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 0 Upper Limit: 3600 | Sets maximum idle warmup time. Warmup time may be less if coolant temperature exceeds threshold | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43682 | Load Dump Activation Method | Read/Write | 0: Overload 1: Underfrequency 2: Overload or Underfrequency 3: Disabled | Enables the load dump output as a function of the overload and underfrequency conditions | PC 2.x, PC 3.x |
| 43683 | Load Dump Overload Set Time | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 0 Upper Limit: 120 | The time delay until the load dump overload condition is set active | PC 2.x, PC 3.x |
| 43684 | Load Dump Overload Threshold | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: % Lower Limit: 80 Upper Limit: 140 | The load dump overload threshold as a percentage of the generator set application rating | PC 2.x, PC 3.x |
| 43685 | Load Dump Underfrequen cy Offset | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: Hz Lower Limit: 0 Upper Limit: 10 | The frequency amount which the load dump underfrequency threshold is below the final frequency reference | PC 2.x, PC 3.x |
| 43686 | Load Dump Underfrequen cy Set Time | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 0 Upper Limit: 20 | The time delay until the load dump underfrequency condition is set active | PC 2.x, PC 3.x |
| 43687 | Load Dump Underfrequen cy Threshold | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Hz Lower Limit: 0 Upper Limit: 90 | The frequency trip threshold for the load dump underfrequency condition | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43688 | Low Battery Voltage Set Time | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 2 Upper Limit: 60 | The time delay until a low battery voltage condition is reported as a fault | PC 2.x, PC 3.x |
| 43689 | Low Fuel in Day Tank Time | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 0 Upper Limit: 20 | Low Fuel in Day Tank Fault time delay from switch input | PC 2.x, PC 3.x |
| 43690 | Low Fuel Set/Clear Time | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 2 Upper Limit: 60 | A trim that sets the delay time for generating the inactive and active faults | PC 2.x, PC 3.x |
| 43691 | Manual Warmup Bypass | Read/Write | 0: Normal 1: Bypass Warmup | Use to command idle speed or to bypass idle warmup during a manual run | PC 2.x, PC 3.x |
| 43692 | Max Idle Time | Read/Write | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: minutes Lower Limit: 0 Upper Limit: 20 | Sets the fault time for the Too Long in Idle fault | PC 2.x, PC 3.x |
| 43693 | Nominal Battery Voltage | Read Only | 0: 12V 1: 24V | Selects the generator set’s nominal battery operating voltage | PC 2.x, PC 3.x |
| 43694 | Prelube Cycle Enable | Read/Write | 0: Disabled 1: Enabled | Enables Or Disables the cyclic mode of prelube operation | PC 2.x, PC 3.x |
| 43695 | Prelube Cycle Time | Read/Write | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: hours Lower Limit: 1 Upper Limit: 10000 | Sets the period of the Prelube Cycle Iteration | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43696 | Prelube Function Enable | Read/Write | 0: Disabled 1: Enabled | Selects whether the Prelube function is enabled or disabled. This is Setup mode interlocked | PC 2.x, PC 3.x |
| 43697 | Prelube Oil Pressure Threshold | Read/Write | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: psig Lower Limit: 0 Upper Limit: 10 | The oil pressure value which when reached the prelube driver will turn off | PC 2.x, PC 3.x |
| 43698 | Prelube Timeout Period | Read/Write | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 0 Upper Limit: 30 | Sets the maximum time for which the Prelube Driver will Remain ON | PC 2.x, PC 3.x |
| 43699 | Rated to Idle Ramp Time | Read/Write | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 0 Upper Limit: 30 | The time over which the speed reference is to ramp from rated speed to idle speed | PC 2.x, PC 3.x |
| 43700 | Utility Availability Status | Read Only | 0: Not Available 1: Available 2: Unknown | Indicates status of the utility source | PC 3.x |
| 43701 | Utility CB Inhibit Command | Read Only | 0: Inactive 1: Active | Utility cb inhibit command | PC 3.x |
| 43702 | Utility CB Tripped Command | Read Only | 0: Inactive 1: Active | Utility cb tripped command | PC 3.x |
| 43703 | Utility Current Based Breaker Position | Read Only | 0: Unknown 1: Closed | Indicates utility breaker position based on current | PC 3.x |
| 43704 | Utility Frequency Lower Drop- Out Threshold | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Hz Lower Limit: Upper Limit: | Indicates the lower drop-out threshold in Hz for utility frequency sensor | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43705 | Utility Frequency Lower Pick- Up Threshold | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Hz Lower Limit: Upper Limit: | Indicates the lower pick-up threshold in Hz for utility frequency sensor | PC 3.x |
| 43706 | Utility Frequency Sensor Status | Read Only | 0: Unknown 1: Picked Up 2: Dropped Out | Indicates utility frequency sensor status | PC 3.x |
| 43707 | Utility Frequency Upper Drop- Out Threshold | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Hz Lower Limit: Upper Limit: | Indicates the upper drop-out threshold in Hz for utility frequency sensor | PC 3.x |
| 43708 | Utility Frequency Upper Pick- Up Threshold | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Hz Lower Limit: Upper Limit: | Indicates the upper pick-up threshold in Hz for utility frequency sensor | PC 3.x |
| 43709 | Utility Loss of Phase Sensor Status | Read Only | 0: Unknown 1: Picked Up 2: Dropped Out | Indicates utility loss of phase sensor status | PC 3.x |
| 43710 | Utility Overvoltage Drop-Out Threshold | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit: | Indicates the drop-out threshold in volts for utility over voltage sensor | PC 3.x |
| 43711 | Utility Overvoltage Pick-Up Threshold | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit: | Indicates the pick-up threshold in volts for utility over voltage sensor | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43712 | Utility Overvoltage Sensor Status | Read Only | 0: Unknown 1: Picked Up 2: Dropped Out | Indicates utility over voltage sensor status | PC 3.x |
| 43713 | Utility Phase Rotation Sensor Status | Read Only | 0: Unknown 1: Picked Up 2: Dropped Out | Indicates utility phase rotation sensor status | PC 3.x |
| 43714 | Utility Undervoltage Drop-Out Threshold | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit: | Indicates the drop-out threshold in volts for utility under voltage sensor | PC 3.x |
| 43715 | Utility Undervoltage Pick-Up Threshold | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Vac Lower Limit: Upper Limit: | Indicates the pick-up threshold in volts for utility under voltage sensor | PC 3.x |
| 43716 | Utility Undervoltage Sensor Status | Read Only | 0: Unknown 1: Picked Up 2: Dropped Out | Indicates utility under voltage sensor status | PC 3.x |
| 43717 | Voltage Droop Enable Command | Read Only | 0: Inactive 1: Active | Command value of voltage droop enable | PC 2.x, PC 3.x |
| 43719 | Alternator Temperature 1 (Aux101) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: -32767 Upper Limit: 32762 | Monitor point for the Alternator Temperature 1 input from the Aux 101 I/O module. | PC 2.x, PC 3.x |
| 43720 | Alternator Temperature 2 (Aux101) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: -32767 Upper Limit: 32762 | Monitor point for the Alternator Temperature 2 input from the Aux 101 I/O module. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43721 | Alternator Temperature 3 (Aux101) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: -32767 Upper Limit: 32762 | Monitor point for the Alternator Temperature 3 input from the Aux 101 I/O module. | PC 2.x, PC 3.x |
| 43722 | Ambient Temperature (Aux101) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: -32767 Upper Limit: 32762 | Monitor point for the Ambient Temperature input from the Aux 101 I/O module. | PC 2.x, PC 3.x |
| 43723 | Aux101 0 Analog Input 1 Voltage | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: S Unit: Vdc Lower Limit: -500 Upper Limit: 500 | Monitor point for the module 0 analog input 1 in volts | PC 2.x, PC 3.x |
| 43724 | Aux101 0 Analog Input 2 Voltage | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: S Unit: Vdc Lower Limit: -500 Upper Limit: 500 | Monitor point for the module 0 analog input 2 in volts | PC 2.x, PC 3.x |
| 43725 | Aux101 0 Analog Input 3 Voltage | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: S Unit: Vdc Lower Limit: Upper Limit: | Monitor point for the module 0 analog input 3 in volts | PC 2.x, PC 3.x |
| 43726 | Aux101 0 Analog Input 4 Voltage | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: S Unit: Vdc Lower Limit: Upper Limit: | Monitor point for the module 0 analog input 4 in volts | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43727 | Aux101 0 Analog Input 5 Voltage | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: S Unit: Vdc Lower Limit: Upper Limit: | Monitor point for the module 0 analog input 5 in volts | PC 2.x, PC 3.x |
| 43728 | Aux101 0 Analog Input 6 Voltage | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: S Unit: Vdc Lower Limit: Upper Limit: | Monitor point for the module 0 analog input 6 in volts | PC 2.x, PC 3.x |
| 43729 | Aux101 0 Analog Input 7 Voltage | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: S Unit: Vdc Lower Limit: Upper Limit: | Monitor point for the module 0 analog input 7 in volts | PC 2.x, PC 3.x |
| 43730 | Aux101 0 Analog Input 8 Voltage | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: S Unit: Vdc Lower Limit: Upper Limit: | Monitor point for the module 0 analog input 8 in volts | PC 2.x, PC 3.x |
| 43731 | Aux101 1 Analog Input 1 Voltage | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: S Unit: Vdc Lower Limit: -500 Upper Limit: 500 | Monitor point for the module 1 analog input 1 in volts | PC 2.x, PC 3.x |
| 43732 | Aux101 1 Analog Input 2 Voltage | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: S Unit: Vdc Lower Limit: -500 Upper Limit: 500 | Monitor point for the module 1 analog input 2 in volts | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43733 | Aux101 1 Analog Input 3 Voltage | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: S Unit: Vdc Lower Limit: Upper Limit: | Monitor point for the module 1 analog input 3 in volts | PC 2.x, PC 3.x |
| 43734 | Aux101 1 Analog Input 4 Voltage | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: S Unit: Vdc Lower Limit: Upper Limit: | Monitor point for the module 1 analog input 4 in volts | PC 2.x, PC 3.x |
| 43735 | Aux101 1 Analog Input 5 Voltage | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: S Unit: Vdc Lower Limit: Upper Limit: | Monitor point for the module 1 analog input 5 in volts | PC 2.x, PC 3.x |
| 43736 | Aux101 1 Analog Input 6 Voltage | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: S Unit: Vdc Lower Limit: Upper Limit: | Monitor point for the module 1 analog input 6 in volts | PC 2.x, PC 3.x |
| 43737 | Aux101 1 Analog Input 7 Voltage | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: S Unit: Vdc Lower Limit: Upper Limit: | Monitor point for the module 1 analog input 7 in volts | PC 2.x, PC 3.x |
| 43738 | Aux101 1 Analog Input 8 Voltage | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: S Unit: Vdc Lower Limit: Upper Limit: | Monitor point for the module 1 analog input 8 in volts | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43739 | Battery Charger AC Failure (HMI113) | Read Only | 0: Inactive 1: Active | Monitor point for the battery charger failure input from the PCCNet annunciator. | PC 2.x, PC 3.x |
| 43740 | Drive End Bearing Temperature (Aux101) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: -32767 Upper Limit: 32762 | Monitor point for the Drive End Bearing Temperature input from the I/O module. | PC 2.x, PC 3.x |
| 43741 | Exhaust Stack Temperature 1 (Aux101) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: -32767 Upper Limit: 32762 | Monitor point for the Exhaust Stack Temperature1 input from the I/O module. | PC 2.x, PC 3.x |
| 43742 | Exhaust Stack Temperature 2 (Aux101) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: -32767 Upper Limit: 32762 | Monitor point for the Exhaust Stack Temperature2 input from the I/O module. | PC 2.x, PC 3.x |
| 43745 | Fuel Level % (PCCNet) | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: % Lower Limit: Upper Limit: | Monitor point for the % fuel level input from the I/O module. | PC 2.x, PC 3.x |
| 43746 | Fuel Level (PCCNet) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: Lower Limit: Upper Limit: | Monitor point for the fuel level (in gallons) input from the I/O module. | PC 2.x, PC 3.x |
| 43747 | HMI113 Fault 1 Status | Read Only | 0: Inactive 1: Active | Monitor point for input #1 from the annunciator. | PC 2.x, PC 3.x |
| 43748 | HMI113 Fault 2 Status | Read Only | 0: Inactive 1: Active | Monitor point for input #2 from the annunciator. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43749 | HMI113 Fault 3 Status | Read Only | 0: Inactive 1: Active | Monitor point for the input #3 from the annunciator. | PC 2.x, PC 3.x |
| 43750 | Intake Manifold Temperature 1 (Aux101) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: -32768 Upper Limit: 32762 | Monitor point for the Intake Manifold Temperature 1 input from the I/O module. | PC 2.x, PC 3.x |
| 43751 | Low Coolant Level (HMI113) | Read Only | 0: Inactive 1: Active | Monitor point for the Low Coolant Level input from the PCCNet annunciator. | PC 2.x, PC 3.x |
| 43752 | Low Fuel Level (HMI113) | Read Only | 0: Inactive 1: Active | Monitor point for the Low Fuel Level input from the PCCNet annunciator. | PC 2.x, PC 3.x |
| 43755 | Non-Drive End Bearing Temperature (Aux101) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: -32768 Upper Limit: 32762 | Monitor point for the Non- Drive End Bearing Temperature input from the I/O module. | PC 2.x, PC 3.x |
| 43756 | Number of Connected Bargraph Modules | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 255 | Used to monitor the amount of connected bargraph modules. | PC 2.x, PC 3.x |
| 43757 | Oil Temperature (Aux101) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: -65534 Upper Limit: 65535 | Monitor point for the Oil Temperature input from the I/O Module. | PC 2.x, PC 3.x |
| 43758 | Modbus Bus Message Count | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: Upper Limit | Modbus bus message count | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43759 | Modbus CRC Errors Count | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: Upper Limit | Modbus CRC errors count | PC 2.x, PC 3.x |
| 43760 | Modbus Exception Count | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: Upper Limit | Modbus exception count | PC 2.x, PC 3.x |
| 43761 | Modbus No Response Count | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: Upper Limit | Modbus no response count | PC 2.x, PC 3.x |
| 43762 | Modbus Slave Message Count | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: Upper Limit | Modbus slave message count | PC 2.x, PC 3.x |
| 43763 | Frequency Match Error | Read Only | Multiplier: 0.001 Offset: 0 Size (bits): 16 Sign: S Unit: Hz Lower Limit: Upper Limit | frequency match error value used by frequency match PI loop | PC 3.x |
| 43764 | Frequency Match Offset | Read Only | Multiplier : 0.001 Offset: 0 Size (bits): 16 Sign: S Unit: Hz Lower Limit: Upper Limit Default: NA | Offset to the frequency match error calculation | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43765 | Load Dump Request | Read Only | 0: Inactive 1: Active | Indicates a load dump is desired due to load exceeding derate level. | PC 2.x, PC 3.x |
| 43766 | Load Govern kVAR Ramp State | Read Only | 0: Not Applicable 1: Ramp Load 2: Track Target 3: Ramp Unload 4: Ramp Unload Complete | Indicates status of load govern kVAR ramping control | PC 3.x |
| 43767 | Load Govern kVAR Target | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: S Unit: % Lower Limit: Upper Limit Default: NA | Indicates the final target setpoint for generator set kVAR output when paralleled to utility | PC 3.x |
| 43768 | Load Govern kW Ramp State | Read Only | 0: Not Applicable 1: Ramp Load 2: Track Target 3: Ramp Unload 4: Ramp Unload Complete | Indicates status of load govern kW ramping control | PC 3.x |
| 43769 | Load Govern kW Target | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: S Unit: % Lower Limit: Upper Limit Default: NA | Indicates the final target setpoint for generator set kW output when paralleled to utility | PC 3.x |
| 43770 | Permissive Close Allowed | Read Only | 0: Not Allowed 1: Allowed | Indicates when permissive sync check conditions have been met | PC 3.x |
| 43772 | Permissive Phase Match Error | Read Only | Multiplier : 0.01 Offset: 0 Size (bits): 16 Sign: S Units: deg Lower Limit: NA Upper Limit: NA Default: NA | Phase error signal for the permissive sync check algorithm | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43773 | Phase Match Error | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: S Units: deg Lower Limit: Upper Limit: | Phase error signal for the synchronizer control algorithm | PC 3.x |
| 43774 | Ramp Load/Unload Command | Read Only | 0: Load 1: Unload | Indicates overall status of ramp load unload inputs | PC 3.x |
| 43775 | Utility Unloaded Status | Read Only | 0: Not Available 1: Not Unloaded 2: Unloaded | Indicates unloaded status of the utility source | PC 3.x |
| 43776 | Genset CB Close Status | Read Only | 0: Inactive 1: Active | Indicates if the output’s status is Inactive or Active | PC 3.x |
| 43777 | Start Type/Configu rable Input #11 Switch | Read Only | 0: Inactive 1: Active | This is the status of the Configurable Input #11. | PC 2.x, PC 3.x |
| 43778 | Scheduler Run Command | Read Only | 0: Off 1: No Load 2: With Load 3: Extended Parallel | Indicates the current run command coming from the scheduler. | PC 2.x, PC 3.x |
| 43785 | Start Attempts Since Reset | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: Lower Limit: 0 Upper Limit: 4294967290 | Number of start attempts since the last reset. | PC 2.x, PC 3.x |
| 43786 | Start Attempts Since Reset | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: Lower Limit: 0 Upper Limit: 4294967290 | Number of start attempts since the last reset. | PC 2.x, PC 3.x |
| 43787 | Total Start Attempts | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: Lower Limit: 0 Upper Limit: 4294967290 | Total number of start attempts. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43788 | Total Start Attempts | Read Only | Multiplier: 1 Offset: 0 Size (bits): 32 Sign: U Unit: Lower Limit: 0 Upper Limit: 4294967290 | Total number of start attempts. | PC 2.x, PC 3.x |
| 43789 | Backup Start Disconnect/C onfigurable Input #33 Switch | Read Only | 0: Inactive 1: Active | This is the status of the Configurable Input #33. | PC 3.x |
| 43790 | Backup Start Disconnect Switch | Read Only | 0: Inactive 1: Active | Status of the Backup Start Disconnect Switch Input | PC 3.x |
| 43791 | Battery Charger Failed Switch | Read Only | 0: Inactive 1: Active | Battery Charger Failed Switch function output status; gives software Inactive/Active state | PC 2.x, PC 3.x |
| 43792 | Battle Short Switch | Read Only | 0: Inactive 1: Active | Battle Short Switch function output status (Active or Inactive) | PC 2.x, PC 3.x |
| 43793 | Configurable Input #1 Switch | Read Only | 0: Inactive 1: Active | Configurable Input #1 input software state status. Gives software Inactive/Active state | PC 2.x, PC 3.x |
| 43794 | Configurable Input #2 Switch | Read Only | 0: Inactive 1: Active | Configurable Input #2 input software state status. Gives software Inactive/Active state | PC 2.x, PC 3.x |
| 43795 | Configurable Input #13 Switch | Read Only | 0: Inactive 1: Active | Configurable Input #13 input software state status. Gives software Inactive/Active state | PC 2.x, PC 3.x |
| 43796 | Genset CB Open Command | Read Only | 0: Inactive 1: Active | Generator set cb open command status | PC 3.x |
| 43797 | Number of Connected Battery Chargers | Read Only | Multiplier : 1 Offset: 0 Size (bits): 8 Sign: U Units: NA Lower Limit: 0 Upper Limit: 255 Default: NA | Used to monitor the amount of connected Battery Chargers | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43800 | Rated Cooldown Time | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 0 Upper Limit: 600 | Minimum time to spend at rated speed less than 10% load before normal shutdown is allowed | PC 2.x, PC 3.x |
| 43801 | Rated to Idle Transition Delay | Read/Write | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 0 Upper Limit: 10 | Sets the delay time for transitioning from Rated to Idle speed. 0 seconds = feature is disabled. | PC 2.x, PC 3.x |
| 43802 | Rupture Basin Time | Read/Write | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 0 Upper Limit: 20 | Rupture Basin fault time delay | PC 2.x, PC 3.x |
| 43803 | Start Time Delay | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 0 Upper Limit: 300 | Sets the time to wait from receiving a valid remote start signal until starting the generator set | PC 2.x, PC 3.x |
| 43804 | Starting to Rated Ramp Time | Read/Write | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 0 Upper Limit: 300 | The time over which the speed reference is to ramp from starting speed to rated speed | PC 2.x, PC 3.x |
| 43805 | Time Delay to Stop | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 0 Upper Limit: 600 | Sets time to run at rated speed before going to cooldown at idle. Does not apply to manual runs | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43806 | Voltage Adjust | Read/Write | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: S Unit: % Lower Limit: -5 Upper Limit: 5 | A trim that allows the user to add/subtract an offset to the nominal voltage when calculating the voltage setpoint | PC 2.x, PC 3.x |
| 43807 | Voltage Ramp Time | Read/Write | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 0 Upper Limit: 5 | The time period over which the voltage setpoint command should rise from 0% to the target voltage | PC 2.x, PC 3.x |
| 43808 | Commit to Transfer State | Read Only | 0: Not Committed 1: Committed | PTC - Indicates if system is committed to transferring to generator set | PC 3.x |
| 43810 | Battle Short Switch (Modbus) | Read/Write | 0: Inactive 1: Committed | Trim to enable Battle Short via Modbus. | PC 2.x, PC 3.x |
| 43811 | Exercise Switch (Modbus) | Read/Write | 0: Inactive 1: Active | Modbus exercise switch | PC 2.x, PC 3.x |
| 43813 | Extended Parallel Switch (Modbus) | Read/Write | 0: Inactive 1: Active | Modbus extended parallel switch | PC 2.x, PC 3.x |
| 43814 | PTC Mode Switch (Modbus) | Read/Write | 0: Inactive 1: Active | Modbus PTC Mode switch | PC 3.x |
| 43815 | Start Type (Modbus) | Read/Write | 0: Emergency 1: Non Emergency | Modbus start type switch | PC 2.x, PC 3.x |
| 43816 | Sync Disable | Read / Write | 0: Inactive 1: Active | Use to turn off synchronizer for testing purposes | PC 3.x |
| 43817 | Genset Circuit Breaker Inhibit | Read/Write | 0: Inactive 1: Active | Identical operation to the configurable input of the same name. Opens genset breaker if closed; inhibits closure if genset breaker is open | PC 3.x |
| 43818 | Isolated Bus Speed Control Method | Read/Write | 0: Constant 1: Droop | Sets the speed control method for isolated bus paralleling. Parameter is also known as Load Share Speed Droop Control Method | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43819 | Isolated Bus Voltage Control Method | Read/Write | 0: Constant 1: Droop | Sets the voltage control method for isolated bus paralleling | PC 2.x, PC 3.x |
| 43820 | Maximum Parallel Time (TDMP) | Read/Write | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 0 Upper Limit: 1800 | Sets the maximum time that the generator set can remain paralleled to the utility during closed transition transfers | PC 3.x |
| 43821 | Programmed Transition Delay (TDPT) | Read/Write | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 0 Upper Limit: 60 | Sets the time delay from when one source opens until the other closes during open transition transfers | PC 3.x |
| 43822 | Retransfer Delay (TDEN) | Read/Write | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 0 Upper Limit: 1800 | Sets the amount of time that the utility source must be available before the control will retransfer to that source. | PC 3.x |
| 43823 | Synchronizer Speed Control Method | Read/Write | 0: Phase Match 1: Slip Frequency 2: External | Sets the speed control method for synchronizing. | PC 3.x |
| 43824 | Synchronizer Voltage Control Method | Read/Write | 0: Voltage Match 1: External | Sets the voltage control method for synchronizing. | PC 3.x |
| 43825 | Transfer Delay (TDNE) | Read/Write | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 0 Upper Limit: 120 | Sets the amount of time that the generator set source must be available before the control will transfer to that source. | PC 3.x |
| 43826 | Transition Type | Read/Write | 0: Open Transition 1: Hard Closed Transition 2: Soft Closed Transition | Sets the load transfer transition type for use when Generator set Application Type = Power Transfer Control. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43827 | Retransfer Inhibit | Read/Write | 0: Inactive 1: Active | Identical operation to the configurable input of the same name. Normally inhibits retransfer to the utility; under some conditions it is ignored; not the same as utility circuit breaker inhibit. | PC 3.x |
| 43828 | Utility Circuit Breaker Inhibit | Read/Write | 0: Inactive 1: Active | Identical operation to the configurable input of the same name. Opens utility main if closed; inhibits closure if utility main is open. | PC 3.x |
| 43829 | Utility Parallel Speed Control Method | Read/Write | 0: Load Govern 1: Droop | Sets the speed control method for utility paralleling. | PC 3.x |
| 43830 | Utility Parallel Voltage Control Method | Read/Write | 0: Load Govern 1: Droop 2: Load Govern with Droop Feed Forward | Sets the voltage control method for utility paralleling. | PC 3.x |
| 43831 | Aux101 Device 0 PCCNet Failure Response Type | Read/Write | 0: Critical Device Response 1: Non-Critical Device Response | Selects the generator set reaction to a loss of a Device 0 I/O module as critical (Shutdown) or non-critical (Warning). | PC 2.x, PC 3.x |
| 43832 | Aux101 Device 1 PCCNet Failure Response Type | Read/Write | 0: Critical Device Response 1: Non-Critical Device Response | Selects the generator set reaction to a loss of a Device 1 I/O module as critical (Shutdown) or non-critical (Warning). | PC 2.x, PC 3.x |
| 43834 | HMI113 Annunciator PCCNet Failure Response Type | Read/Write | 0: Critical Device Response 1: Non-Critical Device Response | Selects the generator set reaction to a loss of an annunciator as critical or non- critical. Selecting critical will cause a shutdown when the annunciator loses communication. | PC 2.x, PC 3.x |
| 43835 | HMI1xx PCCNet Failure Response Type | Read / Write | 0: Critical Device Response 1: Non-Critical Device Response | Selects the genset reaction to a loss of an HMI1xx Operator Panel as critical or non- critical. A critical response will shutdown the genset when PCCNet communication is lost. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43836 | HMI220 PCCNet Failure Response Type | Read/Write | 0: Critical Device Response 1: Non-Critical Device Response | Selects the generator set reaction to a loss of an HMI220 operator panel as critical or non-critical. A critical response will shutdown the generator set when PCCNet communication is lost. | PC 2.x, PC 3.x |
| 43837 | HMI320 PCCNet Failure Response Type | Read/Write | 0: Critical Device Response 1: Non-Critical Device Response | Selects the generator set reaction to a loss of an HMI320 operator panel as critical or non-critical. A critical response will shutdown the generator set when PCCNet communication is lost. | PC 2.x, PC 3.x |
| 43838 | HMI4xx PCCNet Failure Response Type | Read / Write | 0: Critical Device Response 1: Non-Critical Device Response | Selects the genset reaction to a loss of an HMI4xx Operator Panel as critical or non- critical. A critical response will shutdown the genset when PCCNet communication is lost. | PC 2.x PC 3.x |
| 43839 | PCCNet Device Failure Time Delay | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 0 Upper Limit: 250 | Selects the time allowed for arbitration to occur before a PCCNet failure fault is generated. | PC 2.x, PC 3.x |
| 43840 | Test With Load Enable | Read/Write | 0: Disabled 1: Enabled | Use to choose whether a test is with load or without load. | PC 3.x |
| 43841 | Transfer Inhibit | Read/Write | 0: Inactive 1: Active | Identical operation to the configurable input of the same name. Normally inhibits transfer to the genset; under some conditions it is ignored; not the same as genset circuit breaker inhibit. | PC 3.x |
| 43842 | Commit to Transfer Method | Read/Write | 0: Utility Disconnect 1: Genset Start 2: No Commit | PTC - sets point at which system commits to transfer to generator set | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43843 | Commit to Transfer Timeout | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 0 Upper Limit: 3200 | PTC - sets time system will wait for generator set when committed to transfer | PC 3.x |
| 43844 | Commit to Transfer Timer | Read Only | Multiplier: 0.05 Offset: 0 Size (bits): 16 Sign: U Unit: sec Lower Limit: Upper Limit: | PTC - remaining time system to wait for generator set when committed to transfer | PC 3.x |
| 43845 | Modbus Failure Time Delay | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 0 Upper Limit: 10 | Time delay before the control activates the Modbus failure fault after the Master is sensed as no longer present. | PC 2.x, PC 3.x |
| 43846 | Modbus Communicati ons Lost Response Method | Read/Write | 0: Do Nothing 1: Reset Commands | When set to Reset Commands will reset the Modbus control logicals to an inactive state when Modbus communications are lost | PC 2.x, PC 3.x |
| 43847 | Modbus Clear Counters | Read/Write | 0: Do Nothing 1: Clear Counters | Resets all Modbus counters, including J14 if applicable. | PC 2.x, PC 3.x |
| 43848 | Controlled Shutdown Max Ramp Unload Time | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 0 Upper Limit: 300 | maximum ramp unload time during a shutdown with cooldown | PC 3.x |
| 43849 | Genset kVAR Setpoint | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: kVAR Lower Limit: -20000 Upper Limit: 20000 | Sets the generator set load govern kVAR base load internal operating setpoint in units of kVAR. Requires that Load Govern kVAR Setpoint Source = Internal and Load Govern kVAR Method = generator set kVAR. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43850 | Genset kVAR Setpoint Percent | Read/Write | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: S Unit: % Lower Limit: -60 Upper Limit: 60 | Sets the generator set load govern kVAR base load internal operating setpoint in % of standby kVA rating. Requires that Load Govern kVAR Setpoint Source = Internal and Load Govern kVAR Method = generator set kVAR. | PC 3.x |
| 43851 | Genset kW Setpoint | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: kW Lower Limit: 0 Upper Limit: 20000 | Sets the generator set load govern kW base load internal operating setpoint in units of kW. Requires that Load Govern kW Setpoint Source = Internal and Load Govern kW Method = Genset kW. | PC 3.x |
| 43852 | Genset kW Setpoint Percent | Read/Write | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: S Unit: % Lower Limit: 0 Upper Limit: 100 | Sets the generator set load govern kW base load internal operating setpoint in % of standby rating. Requires that Load Govern kW Setpoint Source = Internal and Load Govern kW Method = Genset kW. | PC 3.x |
| 43853 | Genset Power Factor Setpoint | Read/Write | Multiplier: 0.01 Offset: 0 Size (bits): 8 Sign: S Unit: PF Lower Limit: -1 Upper Limit: 1 | Sets the load govern setpoint for generator set power factor control. Requires that Load Govern kVAR Setpoint Source = Internal and Load Govern kVAR Method = Genset Power Factor. | PC 3.x |
| 43854 | Load Demand Stop (Modbus) | Read/Write | 0: Inactive 1: Active | Modbus input for activating load demand stop on the generator set | PC 3.x |
| 43855 | Load Govern kVAR Method | Read/Write | 0: Genset kVAR 1: Genset Power Factor 2: Utility kVAR 3: Utility Power Factor | Use to select how generator set kVAR output will be controlled when paralleled to utility. | PC 3.x |
| 43856 | Load Govern kVAR Ramp Load Time | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 0 Upper Limit: 900 | Sets load govern kVAR ramp load rate = Genset Standby kVA * 0.6/ this time. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43857 | Load Govern kVAR Ramp Unload Time | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 0 Upper Limit: 900 | Sets load govern kVAR ramp unload rate = Genset Standby kVA * 0.6/ this time. | PC 3.x |
| 43858 | Utility Breaker Opening Point | Read/Write | 0: After Transfer Delay 1: Upon Utility Failure | PTC - point in time at which system opens utility breaker | PC 3.x |
| 43859 | Load Govern kW Ramp Load Time | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 0 Upper Limit: 900 | Sets load govern kW ramp load rate = Genset Standby kW rating/ this time. | PC 3.x |
| 43860 | Load Govern kW Ramp Unload Time | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: seconds Lower Limit: 0 Upper Limit: 900 | Sets load govern kW ramp unload rate = Genset Standby kW rating/ this time. | PC 3.x |
| 43861 | Ramp Load/Unload (Modbus) | Read/Write | 0: Load 1: Unload | Use to control ramp load and unload via Modbus | PC 3.x |
| 43862 | Slip Frequency | Read/Write | Multiplier: 0.001 Offset: 0 Size (bits): 16 Sign: S Unit: Hz Lower Limit: -3 Upper Limit: 3 | Sets the synchronizer slip frequency. Requires that Sync Speed Control Method = Slip Frequency. | PC 3.x |
| 43863 | Utility kVAR Setpoint | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: kVAR Lower Limit: -20000 Upper Limit: 20000 | Sets the utility kVAR peak shave internal operating setpoint in units of kVAR. Requires that Load Govern kVAR Setpoint Source = Internal and Load Govern kVAR Method = Utility kVAR | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43864 | Utility kVAR Setpoint Percent | Read/Write | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: S Unit: % Lower Limit: -320 Upper Limit: 320 | Sets the utility kVAR peak shave internal operating setpoint in % of generator set standby kVA rating. Requires that Load Govern kVAR Setpoint Source = Internal and Load Govern kVAR Method = Utility kVAR. | PC 3.x |
| 43865 | Utility kW Constraint | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: kW Lower Limit: -20000 Upper Limit: 20000 | Sets the utility kW minimum load level for constrained base load mode of operation. Requires that Load Govern kW Setpoint Source = Internal and Load Govern kW Method = Genset kW w/Utility Constraint. | PC 3.x |
| 43866 | Utility kW Constraint Percent | Read/Write | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: S Unit: % Lower Limit: -320 Upper Limit: 320 | Sets utility kW minimum load level for constrained base load mode in % of generator set standby rating. Requires that Load Govern kW Setpoint Source = Internal and Load Govern kW Method = Genset kW w/Utility Constraint. | PC 3.x |
| 43867 | Utility kW Setpoint | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: kW Lower Limit: -20000 Upper Limit: 20000 | Sets the utility kW peak shave internal operating setpoint in units of kW. Requires that Load Govern kW Setpoint Source = Internal and Load Govern kW Method = Utility kW. | PC 3.x |
| 43868 | Utility kW Setpoint Percent | Read/Write | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: S Unit: % Lower Limit: -320 Upper Limit: 320 | Sets the utility kW peak shave internal operating setpoint in % of generator set standby rating. Requires that Load Govern kW Setpoint Source = Internal and Load Govern kW Method = Utility kW. | PC 3.x |
| 43869 | Utility Power Factor Setpoint | Read/Write | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: S Unit: PF Lower Limit: 0.7 Upper Limit: 1 | Sets the internal setpoint for utility power factor control mode when paralleled to utility. Requires that Load Govern kVAR Setpoint Source = Internal and Load Govern kVAR Method = Utility Power Factor. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43870 | Aux101 0 Output 2 Fault/Event | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Parameter to allow for the entry of the fault/event code which will turn the output relay on and off. | PC 2.x, PC 3.x |
| 43871 | Aux101 0 Output 4 Fault/Event | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Parameter to allow for the entry of the fault/event code which will turn the output relay on and off. | PC 2.x, PC 3.x |
| 43872 | Aux101 0 Output 5 Fault/Event | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Parameter to allow for the entry of the fault/event code which will turn the output relay on and off. | PC 2.x, PC 3.x |
| 43873 | Aux101 0 Output 6 Fault/Event | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Parameter to allow for the entry of the fault/event code which will turn the output relay on and off. | PC 2.x, PC 3.x |
| 43874 | Aux101 0 Output 7 Fault/Event | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Parameter to allow for the entry of the fault/event code which will turn the output relay on and off. | PC 2.x, PC 3.x |
| 43875 | Aux101 1 Output 1 Fault/Event | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Parameter to allow for the entry of the fault/event code which will turn the output relay on and off. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43876 | Aux101 1 Output 2 Fault/Event | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Parameter to allow for the entry of the fault/event code which will turn the output relay on and off. | PC 2.x, PC 3.x |
| 43877 | Aux101 1 Output 3 Fault/Event | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Parameter to allow for the entry of the fault/event code which will turn the output relay on and off. | PC 2.x, PC 3.x |
| 43878 | Aux101 1 Output 4 Fault/Event | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Parameter to allow for the entry of the fault/event code which will turn the output relay on and off. | PC 2.x, PC 3.x |
| 43879 | Aux101 1 Output 5 Fault/Event | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Parameter to allow for the entry of the fault/event code which will turn the output relay on and off. | PC 2.x, PC 3.x |
| 43880 | Aux101 1 Output 6 Fault/Event | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Parameter to allow for the entry of the fault/event code which will turn the output relay on and off. | PC 2.x, PC 3.x |
| 43881 | Aux101 1 Output 7 Fault/Event | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Parameter to allow for the entry of the fault/event code which will turn the output relay on and off. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43882 | Aux101 1 Output 8 Fault/Event | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Parameter to allow for the entry of the fault/event code which will turn the output relay on and off. | PC 2.x, PC 3.x |
| 43883 | Aux102 0 Output 10 Fault/Event | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Parameter to allow for the entry of the fault/event code which will turn the output relay on and off. | PC 2.x, PC 3.x |
| 43884 | Aux102 0 Output 11 Fault/Event | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Parameter to allow for the entry of the fault/event code which will turn the output relay on and off. | PC 2.x, PC 3.x |
| 43885 | Aux102 0 Output 12 Fault/Event | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Parameter to allow for the entry of the fault/event code which will turn the output relay on and off. | PC 2.x, PC 3.x |
| 43886 | Aux102 0 Output 13 Fault/Event | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Parameter to allow for the entry of the fault/event code which will turn the output relay on and off. | PC 2.x, PC 3.x |
| 43887 | Aux102 0 Output 14 Fault/Event | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Parameter to allow for the entry of the fault/event code which will turn the output relay on and off. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43888 | Aux102 0 Output 15 Fault/Event | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Parameter to allow for the entry of the fault/event code which will turn the output relay on and off. | PC 2.x, PC 3.x |
| 43889 | Aux102 0 Output 16 Fault/Event | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Parameter to allow for the entry of the fault/event code which will turn the output relay on and off. | PC 2.x, PC 3.x |
| 43890 | Aux102 0 Output 9 Fault/Event | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Parameter to allow for the entry of the fault/event code which will turn the output relay on and off. | PC 2.x, PC 3.x |
| 43891 | Aux102 1 Output 10 Fault/Event | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Parameter to allow for the entry of the fault/event code which will turn the output relay on and off. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43892 | Aux102 1 Output 11 Fault/Event | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Parameter to allow for the entry of the fault/event code which will turn the output relay on and off. | PC 2.x, PC 3.x |
| 43893 | Aux102 1 Output 12 Fault/Event | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Parameter to allow for the entry of the fault/event code which will turn the output relay on and off. | PC 2.x, PC 3.x |
| 43894 | Aux102 1 Output 13 Fault/Event | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Parameter to allow for the entry of the fault/event code which will turn the output relay on and off. | PC 2.x, PC 3.x |
| 43895 | Aux102 1 Output 14 Fault/Event | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Parameter to allow for the entry of the fault/event code which will turn the output relay on and off. | PC 2.x, PC 3.x |
| 43896 | Aux102 1 Output 15 Fault/Event | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Parameter to allow for the entry of the fault/event code which will turn the output relay on and off. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43897 | Aux102 1 Output 16 Fault/Event | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Parameter to allow for the entry of the fault/event code which will turn the output relay on and off. | PC 2.x, PC 3.x |
| 43898 | Aux102 1 Output 9 Fault/Event | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Parameter to allow for the entry of the fault/event code which will turn the output relay on and off. | PC 2.x, PC 3.x |
| 43900 | HMI113 Output 1 Fault/Event | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Parameter to allow for the entry of the fault/event code which will turn the output relay on and off. | PC 2.x, PC 3.x |
| 43901 | HMI113 Output 2 Fault/Event | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Parameter to allow for the entry of the fault/event code which will turn the output relay on and off. | PC 2.x, PC 3.x |
| 43902 | HMI113 Output 3 Fault/Event | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Parameter to allow for the entry of the fault/event code which will turn the output relay on and off. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43903 | HMI113 Output 4 Fault/Event | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Parameter to allow for the entry of the fault/event code which will turn the output relay on and off. | PC 2.x, PC 3.x |
| 43905 | Network Speed Adjust Command | Read/Write | 0: Normal 1: Active | Used to command a fixed 0.5 Hz increase in the speed setpoint | PC 2.x, PC 3.x |
| 43906 | Speed Droop Enable Switch (Modbus) | Read/Write | 0: Inactive 1: Active | Speed droop enable switch input status from Modbus | PC 2.x, PC 3.x |
| 43907 | Voltage Droop Enable Switch (Modbus) | Read/Write | 0: Inactive 1: Active | Voltage droop enable switch input status from Modbus | PC 2.x, PC 3.x |
| 43908 | Genset CB Tripped Switch (Modbus) | Read/Write | 0: Inactive 1: Active | Genset cb tripped from Modbus | PC 3.x |
| 43909 | Utility CB Tripped Switch (Modbus) | Read/Write | 0: Inactive 1: Active | Utility cb tripped switch input from Modbus | PC 3.x |
| 43910 | Save Trims | Read/Write | 0: Do Nothing 1: Save Trims | Save configuration parameters or adjustments to non-volatile memory. Perform Save Trims after all configurations have been updated. Do not save trims unless a change has occurred. | PC 2.x, PC 3.x |
| 43911 | Aux101 0 Output 3 Fault/Event | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Parameter to allow for the entry of the fault/event code which will turn the output relay on and off. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43912 | Aux101 0 Output 1 Fault/Event | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Parameter to allow for the entry of the fault/event code which will turn the output relay on and off. | PC 2.x, PC 3.x |
| 43913 | Aux101 0 Output 8 Fault/Event | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Parameter to allow for the entry of the fault/event code which will turn the output relay on and off. | PC 2.x, PC 3.x |
| 43915 | Extended Parallel Enable | Read/Write | 0: Disabled 1: Enabled | Use to enable the extended paralleling mode of PTC | PC 3.x |
| 43916 | V/Hz Knee Frequency 50Hz | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Hz Lower Limit: 0 Upper Limit: 10 | The voltage will roll off (decrease) proportionally to the V/Hz setup, once the frequency drops below the set point in the V/Hz Knee Frequency. This allows the generator set to recover faster when the frequency drops. This is for 50Hz frequency. | PC 2.x, PC 3.x |
| 43917 | V/Hz Knee Frequency 60Hz | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Hz Lower Limit: 0 Upper Limit: 10 | The voltage will roll off (decrease) proportionally to the V/Hz setup, once the frequency drops below the set point in the V/Hz Knee Frequency. This allows the generator set to recover faster when the frequency drops. This is for 60Hz frequency. | PC 2.x, PC 3.x |
| 43918 | V/Hz Rolloff Slope 50Hz | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: % / Hz Lower Limit: 0 Upper Limit: 10 | The amount of voltage roll off when the frequency is below the knee frequency | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43919 | V/Hz Rolloff Slope 60Hz | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: % / Hz Lower Limit: 0 Upper Limit: 10 | The amount of voltage roll off when the frequency is below the knee frequency | PC 2.x, PC 3.x |
| 43920 | Genset Source Name | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: % / Hz Lower Limit: 0 Upper Limit: 10 | Name for the generator set source. | PC 2.x, PC 3.x |
| 43921 | Genset Source Name | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Name for the generator set source. | PC 2.x, PC 3.x |
| 43922 | Genset Source Name | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Name for the generator set source. | PC 2.x, PC 3.x |
| 43923 | Genset Source Name | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Name for the generator set source. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43924 | Genset Source Name | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Name for the generator set source. | PC 2.x, PC 3.x |
| 43925 | Genset Source Name | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Name for the generator set source. | PC 2.x, PC 3.x |
| 43926 | Genset Source Name | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Name for the generator set source. | PC 2.x, PC 3.x |
| 43927 | Genset Source Name | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Name for the generator set source. | PC 2.x, PC 3.x |
| 43928 | Genset Source Name | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Name for the generator set source. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43929 | Genset Source Name | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Name for the generator set source. | PC 2.x, PC 3.x |
| 43930 | Genset Source Name | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Name for the generator set source. | PC 2.x, PC 3.x |
| 43931 | Genset Source Name | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Name for the generator set source. | PC 2.x, PC 3.x |
| 43932 | Genset Source Name | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Name for the generator set source. | PC 2.x, PC 3.x |
| 43933 | Genset Source Name | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Name for the generator set source. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43934 | Genset Source Name | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Name for the generator set source. | PC 2.x, PC 3.x |
| 43935 | Genset Source Name | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 136 Sign: C Unit: Lower Limit: Upper Limit: | Name for the generator set source. | PC 2.x, PC 3.x |
| 43952 | Speed/Frequ ency Delay | Read/Write | Multiplier: 0.1 Offset: 0 Size (bits): 136 Sign: U Unit: seconds Lower Limit: 0.5 Upper Limit: 10 | Sets the delay time for generating the Speed/Frequency mismatch fault | PC 2.x, PC 3.x |
| 43953 | Speed/Frequ ency Threshold | Read/Write | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Hz Lower Limit: 0.5 Upper Limit: 20 | Sets the threshold for generating the Speed/Frequency mismatch fault | PC 2.x, PC 3.x |
| 43954 | Sync Enable (Modbus) | Read / Write | 0: Inactive 1: Active | Modbus input for enabling the synchronizer | PC 3.x |
| 43955 | Genset Idle Enable | Read Only | 0: Disabled 1: Enabled | Enables or Disable idling of generator set with external governor. | PC 2.x, PC 3.x |
| 43956 | Permissive Frequency Match Error | Read Only | Multiplier : 0.001 Offset: 0 Size (bits): 32 Sign: U Unit: Hz Lower Limit: NA Upper Limit: NA Default: NA | Frequency match error value used by permissive sync check | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43957 | Permissive Frequency Match Error | Read Only | Multiplier : 0.001 Offset: 0 Size (bits): 32 Sign: U Unit: Hz Lower Limit: NA Upper Limit: NA Default: NA | Frequency match error value used by permissive sync check | PC 3.x |
| 43958 | Sync Enable Command | Read Only | 0: Inactive 1: Active | Indicates overall status of sync enable inputs | PC 3.x |
| 43959 | Utility Unloaded Level | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: S Unit: kW Lower Limit: -32768 Upper Limit: 32762 | Sets threshold at which utility source is considered as unloaded. | PC 3.x |
| 43960 | HMI113 Fault 1 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 43961 | HMI113 Fault 1 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 43962 | HMI113 Fault 1 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43963 | HMI113 Fault 1 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 43964 | HMI113 Fault 1 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 43965 | HMI113 Fault 1 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 43966 | HMI113 Fault 1 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 43967 | HMI113 Fault 1 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 43968 | HMI113 Fault 1 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43969 | HMI113 Fault 1 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 43970 | HMI113 Fault 1 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 43971 | HMI113 Fault 1 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 43972 | HMI113 Fault 1 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 43973 | HMI113 Fault 1 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 43974 | HMI113 Fault 1 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43975 | HMI113 Fault 1 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 43976 | HMI113 Fault 1 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 43977 | HMI113 Fault 1 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 43978 | HMI113 Fault 1 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 43979 | HMI113 Fault 1 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 43980 | HMI113 Fault 2 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43981 | HMI113 Fault 2 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 43982 | HMI113 Fault 2 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 43983 | HMI113 Fault 2 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 43984 | HMI113 Fault 2 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 43985 | HMI113 Fault 2 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 43986 | HMI113 Fault 2 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43987 | HMI113 Fault 2 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 43988 | HMI113 Fault 2 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 43989 | HMI113 Fault 2 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 43990 | HMI113 Fault 2 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 43991 | HMI113 Fault 2 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 43992 | HMI113 Fault 2 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43993 | HMI113 Fault 2 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 43994 | HMI113 Fault 2 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 43995 | HMI113 Fault 2 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 43996 | HMI113 Fault 2 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 43997 | HMI113 Fault 2 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 43998 | HMI113 Fault 2 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 43999 | HMI113 Fault 2 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 45999 | Unrecognized SPN/FMI Status | Read Only | 0: All Pairs Recognized 1: Pair Not Recognized | Indicates whether or not all pairs in current DM1 are recognized | PC 2.x, PC 3.x |
| 46000 | Genset Phase Rotation | Read Only | 0: L1-L2-L3 1: L1-L3-L2 2: Not Available | Generator set phase rotation | PC 2.x, PC 3.x |
| 46001 | Utility Phase Rotation | Read Only | 0: L1-L2-L3 1: L1-L3-L2 2: Not Available | Utility phase rotation | PC 3.x |
| 46002 | Genset Bus Phase Rotation | Read Only | 0: L1-L2-L3 1: L1-L3-L2 2: Not Available | Generator set bus phase rotation | PC 3.x |
| 46003 | Base Speed | Read Only | Multiplier: 0.0625 Offset: 0 Size (bits): 32 Sign: U Unit: RPM Lower Limit: Upper Limit: | Provides a point to monitor the base speed | PC 2.x, PC 3.x |
| 46004 | Base Speed | Read Only | Multiplier: 0.0625 Offset: 0 Size (bits): 32 Sign: U Unit: RPM Lower Limit: Upper Limit: | Provides a point to monitor the base speed | PC 2.x, PC 3.x |
| 46005 | Final Speed Reference | Read Only | Multiplier: 0.0625 Offset: 0 Size (bits): 32 Sign: U Unit: RPM Lower Limit: Upper Limit: | Provides a point to monitor the final speed reference | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46006 | Final Speed Reference | Read Only | Multiplier: 0.0625 Offset: 0 Size (bits): 32 Sign: U Unit: RPM Lower Limit: Upper Limit: | Provides a point to monitor the final speed reference | PC 2.x, PC 3.x |
| 46008 | Exhaust Port 1 Temperature | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: -459 Upper Limit: 3155 | Monitor point for the Exhaust Port 1 Temperature | PC 2.x, PC 3.x |
| 46009 | Exhaust Port 2 Temperature | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: -459 Upper Limit: 3155 | Monitor point for the Exhaust Port 2 Temperature | PC 2.x, PC 3.x |
| 46010 | Exhaust Port 3 Temperature | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: -460 Upper Limit: 3155 | Monitor point for the Exhaust Port 3 Temperature | PC 2.x, PC 3.x |
| 46011 | Exhaust Port 4 Temperature | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: -460 Upper Limit: 3155 | Monitor point for the Exhaust Port 4 Temperature | PC 2.x, PC 3.x |
| 46012 | Exhaust Port 5 Temperature | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: -460 Upper Limit: 3155 | Monitor point for the Exhaust Port 5 Temperature | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46013 | Exhaust Port 6 Temperature | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: -460 Upper Limit: 3155 | Monitor point for the Exhaust Port 6 Temperature | PC 2.x, PC 3.x |
| 46014 | Exhaust Port 7 Temperature | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: -460 Upper Limit: 3155 | Monitor point for the Exhaust Port 7 Temperature | PC 2.x, PC 3.x |
| 46015 | Exhaust Port 8 Temperature | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: -460 Upper Limit: 3155 | Monitor point for the Exhaust Port 8 Temperature | PC 2.x, PC 3.x |
| 46016 | Exhaust Port 9 Temperature | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: -460 Upper Limit: 3155 | Monitor point for the Exhaust Port 9 Temperature | PC 2.x, PC 3.x |
| 46017 | Exhaust Port 10 Temperature | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: -460 Upper Limit: 3155 | Monitor point for the Exhaust Port 10 Temperature | PC 2.x, PC 3.x |
| 46018 | Exhaust Port 11 Temperature | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: -460 Upper Limit: 3155 | Monitor point for the Exhaust Port 11 Temperature | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46019 | Exhaust Port 12 Temperature | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: -460 Upper Limit: 3155 | Monitor point for the Exhaust Port 12 Temperature | PC 2.x, PC 3.x |
| 46020 | Exhaust Port 13 Temperature | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: -460 Upper Limit: 3155 | Monitor point for the Exhaust Port 13 Temperature | PC 2.x, PC 3.x |
| 46021 | Exhaust Port 14 Temperature | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: -460 Upper Limit: 3155 | Monitor point for the Exhaust Port 14 Temperature | PC 2.x, PC 3.x |
| 46022 | Exhaust Port 15 Temperature | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: -460 Upper Limit: 3155 | Monitor point for the Exhaust Port 15 Temperature | PC 2.x, PC 3.x |
| 46023 | Exhaust Port 16 Temperature | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: -460 Upper Limit: 3155 | Monitor point for the Exhaust Port 16 Temperature | PC 2.x, PC 3.x |
| 46024 | Exhaust Port 17 Temperature | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: -460 Upper Limit: 3155 | Monitor point for the Exhaust Port 17 Temperature | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46025 | Exhaust Port 18 Temperature | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: -460 Upper Limit: 3155 | Monitor point for the Exhaust Port 18 Temperature | PC 2.x, PC 3.x |
| 46026 | Exhaust Port 19 Temperature | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: -460 Upper Limit: 3155 | Monitor point for the Exhaust Port 19 Temperature | PC 2.x, PC 3.x |
| 46027 | Exhaust Port 20 Temperature | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: -460 Upper Limit: 3155 | Monitor point for the Exhaust Port 20 Temperature | PC 2.x, PC 3.x |
| 46028 | Knock Level Cylinder 1 | Read Only | Multiplier: 1 Offset: 0 Size (bits): 8 Sign: U Unit: % Lower Limit: Upper Limit: | Knock Level for cylinder 1 | PC 3.x |
| 46029 | Knock Level Cylinder 2 | Read Only | Multiplier: 1 Offset: 0 Size (bits): 8 Sign: U Unit: % Lower Limit: Upper Limit: | Knock Level for cylinder 2 | PC 3.x |
| 46030 | Knock Level Cylinder 3 | Read Only | Multiplier: 1 Offset: 0 Size (bits): 8 Sign: U Unit: % Lower Limit: Upper Limit: | Knock Level for cylinder 3 | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46031 | Knock Level Cylinder 4 | Read Only | Multiplier: 1 Offset: 0 Size (bits): 8 Sign: U Unit: % Lower Limit: Upper Limit: | Knock Level for cylinder 4 | PC 3.x |
| 46032 | Knock Level Cylinder 5 | Read Only | Multiplier: 1 Offset: 0 Size (bits): 8 Sign: U Unit: % Lower Limit: Upper Limit: | Knock Level for cylinder 5 | PC 3.x |
| 46033 | Knock Level Cylinder 6 | Read Only | Multiplier: 1 Offset: 0 Size (bits): 8 Sign: U Unit: % Lower Limit: Upper Limit: | Knock Level for cylinder 6 | PC 3.x |
| 46034 | Knock Level Cylinder 7 | Read Only | Multiplier: 1 Offset: 0 Size (bits): 8 Sign: U Unit: % Lower Limit: Upper Limit: | Knock Level for cylinder 7 | PC 3.x |
| 46035 | Knock Level Cylinder 8 | Read Only | Multiplier: 1 Offset: 0 Size (bits): 8 Sign: U Unit: % Lower Limit: Upper Limit: | Knock Level for cylinder 8 | PC 3.x |
| 46036 | Knock Level Cylinder 9 | Read Only | Multiplier: 1 Offset: 0 Size (bits): 8 Sign: U Unit: % Lower Limit: Upper Limit: | Knock Level for cylinder 9 | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46037 | Knock Level Cylinder 10 | Read Only | Multiplier: 1 Offset: 0 Size (bits): 8 Sign: U Unit: % Lower Limit: Upper Limit: | Knock Level for cylinder 10 | PC 3.x |
| 46038 | Knock Level Cylinder 11 | Read Only | Multiplier: 1 Offset: 0 Size (bits): 8 Sign: U Unit: % Lower Limit: Upper Limit: | Knock Level for cylinder 11 | PC 3.x |
| 46039 | Knock Level Cylinder 12 | Read Only | Multiplier: 1 Offset: 0 Size (bits): 8 Sign: U Unit: % Lower Limit: Upper Limit: | Knock Level for cylinder 12 | PC 3.x |
| 46040 | Knock Level Cylinder 13 | Read Only | Multiplier: 1 Offset: 0 Size (bits): 8 Sign: U Unit: % Lower Limit: Upper Limit: | Knock Level for cylinder 13 | PC 3.x |
| 46041 | Knock Level Cylinder 14 | Read Only | Multiplier: 1 Offset: 0 Size (bits): 8 Sign: U Unit: % Lower Limit: Upper Limit: | Knock Level for cylinder 14 | PC 3.x |
| 46042 | Knock Level Cylinder 15 | Read Only | Multiplier: 1 Offset: 0 Size (bits): 8 Sign: U Unit: % Lower Limit: Upper Limit: | Knock Level for cylinder 15 | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46043 | Knock Level Cylinder 16 | Read Only | Multiplier: 1 Offset: 0 Size (bits): 8 Sign: U Unit: % Lower Limit: Upper Limit: | Knock Level for cylinder 16 | PC 3.x |
| 46044 | Knock Level Cylinder 17 | Read Only | Multiplier: 1 Offset: 0 Size (bits): 8 Sign: U Unit: % Lower Limit: Upper Limit: | Knock Level for cylinder 17 | PC 3.x |
| 46045 | Knock Level Cylinder 18 | Read Only | Multiplier: 1 Offset: 0 Size (bits): 8 Sign: U Unit: % Lower Limit: Upper Limit: | Knock Level for cylinder 18 | PC 3.x |
| 46046 | Knock Level Cylinder 19 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 8 Sign: U Unit: % Lower Limit: NA Upper Limit: NA Default: NA | Knock Level for cylinder 19 | PC3.x |
| 46047 | Knock Level Cylinder 20 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 8 Sign: U Unit: % Lower Limit: NA Upper Limit: NA Default: NA | Knock Level for cylinder 20 | PC3.x |
| 46048 | Knock Count Cyl 1 | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Knock count value for cylinder 1 | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46049 | Knock Count Cyl 2 | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Knock count value for cylinder 2 | PC 3.x |
| 46050 | Knock Count Cyl 3 | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Knock count value for cylinder 3 | PC 3.x |
| 46051 | Knock Count Cyl 4 | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Knock count value for cylinder 4 | PC 3.x |
| 46052 | Knock Count Cyl 5 | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Knock count value for cylinder 5 | PC 3.x |
| 46053 | Knock Count Cyl 6 | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Knock count value for cylinder 6 | PC 3.x |
| 46054 | Knock Count Cyl 7 | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Knock count value for cylinder 7 | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46055 | Knock Count Cylr 8 | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Knock count value for cylinder 8 | PC 3.x |
| 46056 | Knock Count Cylinder 9 | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Knock count value for cylinder 9 | PC 3.x |
| 46057 | Knock Count Cylinder 10 | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Knock count value for cylinder 10 | PC 3.x |
| 46058 | Knock Count Cyl 11 | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Knock count value for cylinder 11 | PC 3.x |
| 46059 | Knock Count Cyl 12 | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Knock count value for cylinder 12 | PC 3.x |
| 46060 | Knock Count Cyl 13 | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Knock count value for cylinder 13 | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46061 | Knock Count Cyl 14 | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Knock count value for cylinder 14 | PC 3.x |
| 46062 | Knock Count Cyl 15 | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Knock count value for cylinder 15 | PC 3.x |
| 46063 | Knock Count Cyl 16 | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Knock count value for cylinder 16 | PC 3.x |
| 46064 | Knock Count Cyl 17 | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Knock count value for cylinder 17 | PC 3.x |
| 46065 | Knock Count Cyl 18 | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | Knock count value for cylinder 18 | PC 3.x |
| 46066 | Knock Count Cyl 19 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65530 Default: NA | Knock count value for cylinder 19 | PC3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46067 | Knock Count Cyl 20 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: 0 Upper Limit: 65530 Default: NA | Knock count value for cylinder 20 | PC3.x |
| 46068 | Spark Timing Cyl 1 | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: Degrees Lower Limit: 0 Upper Limit: 65530 Default: NA | Spark timing degrees for cylinder 1 | PC 3.x |
| 46069 | Spark Timing Cyl 2 | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: Degrees Lower Limit: Upper Limit: | Spark timing degrees for cylinder 2 | PC 3.x |
| 46070 | Spark Timing Cyl 3 | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: Degrees Lower Limit: Upper Limit: | Spark timing degrees for cylinder 3 | PC 3.x |
| 46071 | Spark Timing Cyl 4 | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: Degrees Lower Limit: Upper Limit: | Spark timing degrees for cylinder 4 | PC 3.x |
| 46072 | Spark Timing Cyl 5 | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: Degrees Lower Limit: Upper Limit: | Spark timing degrees for cylinder 5 | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46073 | Spark Timing Cyl 6 | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: Degrees Lower Limit: Upper Limit: | Spark timing degrees for cylinder 6 | PC 3.x |
| 46074 | Spark Timing Cyl 7 | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: Degrees Lower Limit: Upper Limit: | Spark timing degrees for cylinder 7 | PC 3.x |
| 46075 | Spark Timing Cyl 8 | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: Degrees Lower Limit: Upper Limit: | Spark timing degrees for cylinder 8 | PC 3.x |
| 46076 | Spark Timing Cyl 9 | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: Degrees Lower Limit: Upper Limit: | Spark timing degrees for cylinder 9 | PC 3.x |
| 46077 | Spark Timing Cyl 10 | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: Degrees Lower Limit: Upper Limit: | Spark timing degrees for cylinder 10 | PC 3.x |
| 46078 | Spark Timing Cyl 11 | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: Degrees Lower Limit: Upper Limit: | Spark timing degrees for cylinder 11 | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46079 | Spark Timing Cyl 12 | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: Degrees Lower Limit: Upper Limit: | Spark timing degrees for cylinder 12 | PC 3.x |
| 46080 | Spark Timing Cyl 13 | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: Degrees Lower Limit: Upper Limit: | Spark timing degrees for cylinder 13 | PC 3.x |
| 46081 | Spark Timing Cyl 14 | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: Degrees Lower Limit: Upper Limit: | Spark timing degrees for cylinder 14 | PC 3.x |
| 46082 | Spark Timing Cyl 15 | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: Degrees Lower Limit: Upper Limit: | Spark timing degrees for cylinder 15 | PC 3.x |
| 46083 | Spark Timing Cyl 16 | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: Degrees Lower Limit: Upper Limit: | Spark timing degrees for cylinder 16 | PC 3.x |
| 46084 | Spark Timing Cyl 17 | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: Degrees Lower Limit: Upper Limit: | Spark timing degrees for cylinder 17 | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46085 | Spark Timing Cyl 18 | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: Degrees Lower Limit: Upper Limit: | Spark timing degrees for cylinder 18 | PC 3.x |
| 46086 | Spark Timing Cyl 19 | Read Only | Multiplier : 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: Degrees Lower Limit: Upper Limit: | Spark timing degrees for cylinder 19 | PC 3.x |
| 46087 | Spark Timing Cyl 20 | Read Only | Multiplier : 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: Degrees Lower Limit: NA Upper Limit: NA Default: NA | Spark timing degrees for cylinder 20 | PC 3.x |
| 46088 | Internal SSM558 1 Temperature | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: Upper Limit: | Temperature of the engine electronic control unit SSM558 1 | PC 3.x |
| 46089 | Internal SSM558 2 Temperature | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: Upper Limit | Temperature of the engine electronic control unit SSM558 2 | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46090 | Internal MCM700 Temperature | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: Upper Limit | Temperature of the engine electronic control unit MCM700 | PC 3.x |
| 46091 | Derate Authorization | Read Only | 0: NO 1: YES 2: Reserved 3: N/A | Derate authorization request from customer. | PC 3.x |
| 46092 | Start System Status | Read Only | 0: Not Tripped 1: Tripped 2: Reserved 3: N/A 4: Network Failure | Start system status monitor point. | PC 3.x |
| 46093 | Ventilator Fan Status | Read Only | 0: OFF 1: ON 2: TRIPPED 3: N/A | Vent Fan status monitor point. | PC 3.x |
| 46094 | Louvres Status | Read Only | 0: Open 1: Closed 2: Reserved 3: N/A 4: Network Failure | Louvres Closed monitor point. | PC 3.x |
| 46095 | Radiator Fan Status | Read Only | 0: OFF 1: ON 2: TRIPPED 3: N/A | Radiator Fan status monitor point. | PC 3.x |
| 46096 | GIB Isolator Open (Aux101) | Read Only | 0: Close 1: Open 2: Reserved 3: N/A | GIB Isolator Open monitor point. | PC 3.x |
| 46097 | Alternator Heater Status | Read Only | 0: OFF 1: ON 2: TRIPPED 3: N/A | Alternator Heater status monitor point. | PC 3.x |
| 46099 | Gearbox Oil Pressure (Aux101) | Read Only | 0: No 1: Yes 2: Reserved 3: N/A 4: Network Failure | Gearbox Oil Pressure monitor point. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46100 | Gearbox Oil Temperature (Aux101) | Read Only | 0: No 1: Yes 2: Reserved 3: N/A 4: Network Failure | Gearbox Oil Temperature monitor point. | PC 3.x |
| 46101 | Start Inhibit No1 (Aux101) | Read Only | 0: Inactive 1: Active 2: Reserved 3: N/A | Start Inhibit No1 monitor point. | PC 3.x |
| 46102 | Start Inhibit No2 (Aux101) | Read Only | 0: Inactive 1: Active 2: Reserved 3: N/A | Start Inhibit No2 monitor point. | PC 3.x |
| 46103 | Start Inhibit No3 (Aux101) | Read Only | 0: Inactive 1: Active 2: Reserved 3: N/A | Start Inhibit No3 monitor point. | PC 3.x |
| 46104 | DC PSU Unavailable (Aux101) | Read Only | 0: No 1: Yes | Engine PSU Not Available monitor point. | PC 3.x |
| 46105 | Ventilator Fan Trip (Aux101) | Read Only | 0: No 1: Yes | Ventilator Fan Trip monitor point. | PC 3.x |
| 46106 | Aux101-3 Software Version | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: Upper Limit | Software version of the firmware for the Aux101-3 | PC 3.x |
| 46107 | Aux101-4 Software Version | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: Upper Limit | Software version of the firmware for the Aux101-4 | PC 3.x |
| 46108 | Aux101-5 Software Version | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: Upper Limit | Software version of the firmware for the Aux101-5 | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46109 | Engine Operating State | Read Only | 0: Engine Stopped 1: Pre-Start 2: Starting 3: Warm-Up 4: Running 5: Cool-Down 6: Engine Stopping 7: Post-Run 8: Out Of Range 9: Out Of Range 10: Out Of Range 11: Out Of Range 12: Out Of Range 13: Out Of Range 14: Out Of Range 15: N/A | Indicate current state or mode of operation by the engine | PC 2.x PC 3.x |
| 46110 | Fuel Pump Control Status | Read Only | 0: Inactive 1: Active 2: Reserved 3: Not Available | Fuel pump state | PC 3.x |
| 46112 | Fuel Shutoff Vent Valve status | Read Only | 0: Closed 1: Open 2: Reserved 3: Not Available | Fuel shutoff valve status | PC 3.x |
| 46113 | Downstream Valve Command Status | Read Only | 0: Open 1: Closed 2: Reserved 3: N/A | The result of the FSO driver output command logic for fuel shutoff valve 1 | PC 3.x |
| 46114 | Upstream Valve Command Status | Read Only | 0: Open 1: Closed 2: Reserved 3: N/A | The result of the FSO driver output command logic for fuel shutoff valve 2. | PC 3.x |
| 46115 | VPS Status | Read Only | 0: OFF 1: ON 2: Reserved 3: N/A | Control setting for fuel shutoff valve proving system test | PC 3.x |
| 46116 | Gas Supply Pressure | Read Only | Multiplier : 0.1 Offset: 0 Size (bits): 16 Sign: U Units: psi Lower Limit: NA Upper Limit: NA Default: NA | Gage Pressure of gas supply to fuel metering device | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46117 | Engine Oil PreHeater Ctrl Status | Read Only | 0: OFF 1: ON 2: Reserved 3: N/A | Engine Oil pre heater command status | PC 3.x |
| 46118 | Engine Power Conservation Ctrl Status | Read Only | 0: OFF 1: ON 2: Reserved 3: Not Available | Control setting for cutting power to various devices when the engine is not in use | PC 3.x |
| 46119 | Engine Coolant PreHeater Ctrl Status | Read Only | 0: OFF 1: ON 2: Reserved 3: N/A | Engine coolant PreHeater states | PC 3.x |
| 46120 | Engine Coolant Pump Ctrl Status | Read Only | 0: OFF 1: ON 2: Reserved 3: N/A | Engine coolant circulating pump status | PC 3.x |
| 46121 | Engine Controlled Shutdown Request | Read Only | 0: Inactive 1: Active 2: Reserved 3: Not Available | Active when the engine control request a controlled shutdown (shutdown with cooldown) | PC 3.x |
| 46122 | Emergency Shutdown Request | Read Only | 0: Inactive 1: Active 2: Reserved 3: Not Available | Active when the engine control request an emergency shutdown (immediate shutdown) | PC 3.x |
| 46123 | Engine Derate Request | Read Only | Multiplier : 0.4 Offset: 0 Size (bits): 8 Sign: U Units: % Lower Limit: NA Upper Limit: NA Default: NA | Derate request in percent made by the engine control | PC 3.x |
| 46124 | Coolant Pressure | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 8 Sign: U Unit: psi Lower Limit: NA Upper Limit: NA | Monitor point for the Coolant Pressure. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46125 | Coolant 2 Pressure | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: psi Lower Limit: 0 Upper Limit: 145 | Monitor point for the Coolant 2 Pressure. | PC 3.x |
| 46127 | Coolant 2 Temperature | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: degF Lower Limit: Upper Limit: | Monitor point for the Coolant 2 Temperature | PC 3.x |
| 46128 | Compressor Bypass Position | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: % Lower Limit: Upper Limit: | Engine turbocharger compressor bypass actuator position | PC 3.x |
| 46129 | Engine Oil Filter Outlet Pressure | Read Only | Multiplier : 0.1 Offset: 0 Size (bits): 16 Sign: U Units: psi Lower Limit: NA Upper Limit: NA Default: NA | ”Engine oil pressure at the outlet of the filter Search ””17185”” (2 hits in 2 files)” | PC 3.x |
| 46130 | Oil Priming Pump Control Status | Read Only | 0: OFF 1: ON 2: Reserved 3: N/A | Status for the priming pump (ON or OFF) | PC 3.x |
| 46131 | Oil Priming State | Read Only | 0: Low 1: Optimum 2: Reserved 3: N/A | Status of the engine before start (Pre-Lubed or Not) | PC 3.x |
| 46132 | Oil Pre- Heated State | Read Only | 0: Cold 1: Heated 2: Reserved 3: N/A | Status of the engine oil before start (Pre-Heated or Not) | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46133 | Coolant Pre- Heated State | Read Only | 0: Cold 1: Heated 2: Reserved 3: N/A | Status of the engine coolant before start (Pre-Heated or Not) | PC 3.x |
| 46134 | Ventilation Status | Read Only | 0: Vented 1: Not Vented 2: Ventilation Delay 3: Currently Venting 4: Reserved 5: Reserved 6: Not Able To Determine 7: Not Available | Engine Ventilation Status (Vented or Not) | PC 3.x |
| 46135 | Intake Manifold Pressure 1 | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Units: psi Lower Limit: NA Upper Limit: NA | Intake Manifold Pressure 1 | PC 3.x |
| 46136 | Compressor Outlet Pressure | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: kPa Lower Limit: NA Upper Limit: NA | Absolute Pressure at the outlet of the compressor. | PC 3.x |
| 46137 | Turbocharger 1 Boost Pressure | Read Only | Multiplier : 0.1 Offset: 0 Size (bits): 16 Sign: U Units: psi Lower Limit: NA Upper Limit: NA Default: NA | Monitor point for the Turbocharger 1 Boost Pressure | PC 3.x |
| 46138 | Genset Avg AC Frequency | Read Only | Multiplier : 0.1 Offset: 0 Size (bits): 16 Sign: U Units: NA Lower Limit: NA Upper Limit: NA Default: NA | Average Genset AC frequency | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46139 | Fuel Valve 1 Inlet Absolute Pressure | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: psi Lower Limit: NA Upper Limit: NA | Absolute Pressure of Gas on the inlet side of the first system control valve | PC 3.x |
| 46140 | Fuel Valve 1 Outlet Absolute Pressure | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: psi Lower Limit: NA Upper Limit: NA | Absolute Pressure of Gas on the outlet side of the first system control valve | PC 3.x |
| 46141 | Fuel Valve 1 Position | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: % Lower Limit: NA Upper Limit: NA |  | PC 3.x |
| 46142 | Fuel Valve 2 Inlet Absolute Pressure | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: psi Lower Limit: NA Upper Limit: NA | Absolute Pressure of Gas on the inlet side of the second system control valve | PC 3.x |
| 46143 | Fuel Valve 2 Outlet Absolute Pressure | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: psi Lower Limit: NA Upper Limit: NA | Absolute Pressure of Gas on the outlet side of the second system control valve | PC 3.x |
| 46144 | Fuel Valve 2 Position | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: % Lower Limit: NA Upper Limit: NA |  | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46145 | Gas Mass Flow | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Pounds per hour Lower Limit: Upper Limit: | Gas Mass Flow value of the engine. | PC 3.x |
| 46146 | Gas Mass Flow | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 32 Sign: U Unit: Pounds per hour Lower Limit: Upper Limit: | Gas Mass Flow value of the engine. | PC 3.x |
| 46147 | Throttle 1 Position | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: % Lower Limit: Upper Limit: | Position of the throttle 1. | PC 3.x |
| 46148 | Throttle 2 Position | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: % Lower Limit: Upper Limit: | Position of the throttle 2. | PC 3.x |
| 46149 | Raw Value DE RTD Bearing | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: Count Lower Limit: NA Upper Limit: NA Default: NA | Raw Value for the DE RTD Bearing from the Aux101 | PC 3.x |
| 46150 | Raw Value Alternator RTD L1 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: Count Lower Limit: NA Upper Limit: NA Default: NA | Raw Value Alternator RTD L1 from Aux101 (10 bits raw data) | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46151 | Raw Value Alternator RTD L2 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: Count Lower Limit: NA Upper Limit: NA Default: NA | Raw Value Alternator RTD L2 from Aux101 (10 bits raw data) | PC 3.x |
| 46152 | Raw Value Alternator RTD L3 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: Count Lower Limit: NA Upper Limit: NA Default: NA | Raw Value Alternator RTD L3 from Aux101 (10 bits raw data) | PC 3.x |
| 46153 | Raw Value NDE RTD Bearing | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: Count Lower Limit: NA Upper Limit: NA Default: NA | Raw Value NDE RTD Bearing from Aux101 (10 bits raw data) | PC 3.x |
| 46155 | MCM700 Battery Voltage | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Vdc Lower Limit: 0 Upper Limit: 65535 Default: NA | Engine Control Module Battery Voltage. | PC 3.x |
| 46157 | CM700 Sensor Voltage A | Read Only | Multiplier : 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Vdc Lower Limit: NA Upper Limit: NA Default: NA | Engine Control Module CM700 Sensor Voltage A | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46158 | CM700 Sensor Voltage B | Read Only | Multiplier : 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Vdc Lower Limit: NA Upper Limit: NA Default: NA | Engine Control Module CM700 Sensor Voltage B | PC 3.x |
| 46159 | CM700 Sensor Voltage C | Read Only | Multiplier : 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Vdc Lower Limit: NA Upper Limit: NA Default: NA | Engine Control Module CM700 Sensor Voltage C | PC 3.x |
| 46160 | SSM558 1 Battery Voltage | Read Only | Multiplier : 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Vdc Lower Limit: NA Upper Limit: NA Default: NA | SSM558 1 Engine Control Module Battery Voltage. | PC 3.x |
| 46161 | SSM558 1 Isolated Battery Voltage | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Vdc Lower Limit: 0 Upper Limit: 65535 Default: NA | SSM558 1 Engine Control Module Isolated Battery Voltage. | PC 3.x |
| 46162 | SSM558 2 Battery Voltage | Read Only | Multiplier : 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Vdc Lower Limit: 0 Upper Limit: 65535 Default: NA | SSM558 2 Engine Control Module Battery Voltage. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46163 | SSM558 2 Isolated Battery Voltage | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Vdc Lower Limit: 0 Upper Limit: 65535 Default: NA | SSM558 2 Engine Control Module Isolated Battery Voltage. | PC 3.x |
| 46164 | Intake Manifold Pressure 2 | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: psi Lower Limit: Upper Limit: | Intake Manifold Pressure 2 | PC 3.x |
| 46165 | Intake Manifold Temperature 2 | Read only | Multiplier : 0.1 Offset: 0 Size (bits): 16 Sign: S Units: degF Lower Limit: -40 Upper Limit: 410 Default: NA | Monitor point for the Intake Manifold Temperature 2 | PC 3.x |
| 46166 | Exhaust Back Pressure | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: psi Lower Limit: -40 Upper Limit: 410 | Monitor point for exhaust back pressure value | PC 3.x |
| 46168 | Air Filter Differential Pressure | Read only | Multiplier : 0.1 Offset: 0 Size (bits): 16 Sign: S Unit: psi Lower Limit: NA Upper Limit: NA Default: NA | Monitor point for air filter differential pressure value | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46170 | Gas Mass Flow 2 | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 16 Sign: U Unit: Pounds per hour Lower Limit: Upper Limit: | Gas Mass Flow 2 value of the engine. | PC 3.x |
| 46171 | Gas Mass Flow 2 | Read Only | Multiplier: 0.1 Offset: 0 Size (bits): 32 Sign: U Unit: Pounds per hour Lower Limit: Upper Limit: | Gas Mass Flow 2 value of the engine. | PC 3.x |
| 46172 | Start Inhibit No.1 OP | Read Only | 0: Inactive 1: Active 2: Reserved 3: Not Available 4: Network Failure | Start Inhibit No.1 OP Monitor Point | PC 3.x |
| 46173 | Start Inhibit No.2 OP | Read Only | 0: Inactive 1: Active 2: Reserved 3: Not Available 4: Network Failure | Start Inhibit No.2 OP Monitor Point | PC 3.x |
| 46174 | Start Inhibit No.3 OP | Read Only | 0: Inactive 1: Active 2: Reserved 3: Not Available 4: Network Failure | Start Inhibit No.3 OP Monitor Point | PC 3.x |
| 46180 | E-Stops disengaged | Read Only | 0: Inactive 1: Active |  | PC 3.x |
| 46176 | Gearbox Present | Read / Write | 0: No 1: Yes | Enables gearbox protection | PC 3.x |
| 46182 | Radiator Fan control | Read Only | 0: Inactive 1: Active | Radiator fan control command | PC 3.x |
| 46183 | Ventilator Fan mode | Read/Write | 0: Limited 1: Continuous | Vent fan control mode, limited or continuous | PC 3.x |
| 46184 | Louvre Control | Read Only | 0: Inactive 1: Active | Louvre control | PC 3.x |
| 46191 | Ventilator Fan control | Read Only | 0: Inactive 1: Active | Ventilator fan control command | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46192 | Engine Spark Plug Voltage 1 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: V Lower Limit: NA Upper Limit: NA | Spark Plug Voltage for Cylinder 1 | PC 3.x |
| 46193 | Engine Spark Plug Voltage 2 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: V Lower Limit: NA Upper Limit: NA Default: NA | Spark Plug Voltage for Cylinder 2 | PC 3.x |
| 46194 | Engine Spark Plug Voltage 3 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: V Lower Limit: NA Upper Limit: NA Default: NA | Spark Plug Voltage for Cylinder 3 | PC 3.x |
| 46195 | Engine Spark Plug Voltage 4 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: V Lower Limit: NA Upper Limit: NA Default: NA | Spark Plug Voltage for Cylinder 4 | PC 3.x |
| 46196 | Engine Spark Plug Voltage 5 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: V Lower Limit: NA Upper Limit: NA Default: NA | Spark Plug Voltage for Cylinder 5 | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46197 | Engine Spark Plug Voltage 6 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: V Lower Limit: NA Upper Limit: NA Default: NA | Spark Plug Voltage for Cylinder 6 | PC 3.x |
| 46198 | Engine Spark Plug Voltage 7 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: V Lower Limit: NA Upper Limit: NA Default: NA | Spark Plug Voltage for Cylinder 7 | PC 3.x |
| 46199 | Engine Spark Plug Voltage 8 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: V Lower Limit: NA Upper Limit: NA Default: NA | Spark Plug Voltage for Cylinder 8 | PC 3.x |
| 46200 | Engine Spark Plug Voltage 9 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: V Lower Limit: NA Upper Limit: NA Default: NA | Spark Plug Voltage for Cylinder 9 | PC 3.x |
| 46201 | Engine Spark Plug Voltage 10 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: V Lower Limit: NA Upper Limit: NA Default: NA | Spark Plug Voltage for Cylinder 10 | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46202 | Engine Spark Plug Voltage 11 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: V Lower Limit: NA Upper Limit: NA Default: NA | Spark Plug Voltage for Cylinder 11 | PC 3.x |
| 46203 | Engine Spark Plug Voltage 12 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: V Lower Limit: NA Upper Limit: NA Default: NA | Spark Plug Voltage for Cylinder 12 | PC 3.x |
| 46204 | Engine Spark Plug Voltage 13 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: V Lower Limit: NA Upper Limit: NA Default: NA | Spark Plug Voltage for Cylinder 13 | PC 3.x |
| 46205 | Engine Spark Plug Voltage 14 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: V Lower Limit: NA Upper Limit: NA Default: NA | Spark Plug Voltage for Cylinder 14 | PC 3.x |
| 46206 | Engine Spark Plug Voltage 15 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: V Lower Limit: NA Upper Limit: NA Default: NA | Spark Plug Voltage for Cylinder 15 | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46207 | Engine Spark Plug Voltage 16 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: V Lower Limit: NA Upper Limit: NA Default: NA | Spark Plug Voltage for Cylinder 16 | PC 3.x |
| 46208 | Engine Spark Plug Voltage 17 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: V Lower Limit: NA Upper Limit: NA Default: NA | Spark Plug Voltage for Cylinder 17 | PC 3.x |
| 46209 | Engine Spark Plug Voltage 18 | Read Only | Multiplier : 1 Offset: 0 Size (bits): 16 Sign: U Units: V Lower Limit: NA Upper Limit: NA Default: NA | Spark Plug Voltage for Cylinder 18 | PC 3.x |
| 46273 | Alternator Heater ON (Aux101) | Read Only | 0: No 1: Yes 2: Reserved 3: N/A 4: Network Failure | Alternator Heater monitor point. | PC 3.x |
| 46288 | DE/NDE Cylinder Viewpoint Reference | Read/Write | 0: Drive End 1: Non-Drive End 2: Reserved 3: N/A | Gives reference point for engine cylinder numbering | PC 3.x |
| 46291 | Radiator Fan Trip (Aux 101) | Read Only | 0: Not Tripped 1: Tripped 2: Reserved 3: N/A | Radiator Fan Trip monitor point. | PC 3.x |
| 46300 | LBNG Genset Enable | Read/Write | 0: Disable 1: Enable | Switch to enable or disable the gas specific features and parameters | PC 3.x |
| 46301 | Aux101-3 Enable | Read/Write | 0: Disable 1: Enable | Enable the processing for Aux101-3 messages | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46302 | Aux101-4 Enable | Read/Write | 0: Disable 1: Enable | Enable the processing for Aux101-4 messages | PC 3.x |
| 46303 | Aux101-5 Enable | Read/Write | 0: Disable 1: Enable | Enable the processing for Aux101-5 messages | PC 3.x |
| 46304 | Aux101-6 Enable | Read/Write | 0: Disable 1: Enable | Enable the processing for Aux101-6 messages | PC 3.x |
| 46308 | Aux101-3 Input Port Config | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 255 | Input Port configuration bye for the Aux101-3 | PC 3.x |
| 46309 | Aux101-4 Input Port Config | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 255 | Input Port configuration bye for the Aux101-4 | PC 3.x |
| 46310 | Aux101-5 Input Port Config | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 255 | Input Port configuration bye for the Aux101-5 | PC 3.x |
| 46311 | Aux101-3 DI Active High/Low Selection | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 255 | Digital Input Port configuration active High or active low for the Aux101-3 | PC 3.x |
| 46312 | Aux101-4 DI Active High/Low Selection | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 255 | Digital Input Port configuration active High or active low for the Aux101-4 | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46313 | Aux101-5 DI Active High/Low Selection | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 255 | Digital Input Port configuration active High or active low for the Aux101-5 | PC 3.x |
| 46314 | Aux101-3 DI Config Mask | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 255 | Discrete Input configuration bit mask for the Aux101-3 | PC 3.x |
| 46315 | Aux101-4 DI Config Mask | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 255 | Discrete Input configuration bit mask for the Aux101-4 | PC 3.x |
| 46316 | Aux101-5 DI Config Mask | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 255 | Discrete Input configuration bit mask for the Aux101-5 | PC 3.x |
| 46323 | Vehicle Electrical Power 2 PGN65165 Enable | Read/Write | 0: Disabled 1: Enabled | A trim that enables the Vehicle Electrical Power 2 message | PC 3.x |
| 46326 | Gaseous Fuel Pressure PGN65163 Enable | Read/Write | 0: Disabled 1: Enabled | A trim that enables the Gaseous Fuel Pressure message | PC 3.x |
| 46327 | Fuel Information 3 - Gaseous PGN64930 Enable | Read/Write | 0: Disabled 1: Enabled | A trim that enables the Fuel Information 3 - Gaseous message | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46328 | Fuel Information 2 - Gaseous PGN65153 Enable | Read/Write | 0: Disabled 1: Enabled | A trim that enables the Fuel Information 2 - Gaseous message | PC 3.x |
| 46332 | Inlet/Exhaust Conditions PGN65270 Enable | Read/Write | 0: Disabled 1: Enabled | A trim that enables the Inlet/Exhaust Conditions message | PC 3.x |
| 46333 | Knock Count 1 PGN65336 Enable | Read/Write | 0: Disabled 1: Enabled | A trim that enables Knock Count 1 message | PC 3.x |
| 46334 | Knock Count 2 PGN65337 Enable | Read/Write | 0: Disabled 1: Enabled | A trim that enables Knock Count 2 message | PC 3.x |
| 46335 | Knock Count 3 PGN65338 Enable | Read/Write | 0: Disabled 1: Enabled | A trim that enables Knock Count 3 message | PC 3.x |
| 46336 | Knock Count 4 PGN65339 Enable | Read/Write | 0: Disabled 1: Enabled | A trim that enables Knock Count 4 message | PC 3.x |
| 46337 | Knock Count 5 PGN65340 Enable | Read/Write | 0: Disabled 1: Enabled | A trim that enables Knock Count 5 message | PC 3.x |
| 46338 | Ignition Timing 1 PGN65154 Enable | Read/Write | 0: Disabled 1: Enabled | A trim that enables the Ignition Timing 1 message | PC 3.x |
| 46339 | Ignition Timing 2 PGN65155 Enable | Read/Write | 0: Disabled 1: Enabled | A trim that enables the Ignition Timing 2 message | PC 3.x |
| 46340 | Ignition Timing 3 PGN65156 Enable | Read/Write | 0: Disabled 1: Enabled | A trim that enables the Ignition Timing 3 message | PC 3.x |
| 46341 | Ignition Timing 4 PGN65157 Enable | Read/Write | 0: Disabled 1: Enabled | A trim that enables the Ignition Timing 4 message | PC 3.x |
| 46342 | Ignition Timing 5 PGN65158 Enable | Read/Write | 0: Disabled 1: Enabled | A trim that enables the Ignition Timing 5 message | PC 3.x |
| 46344 | Start-Enable (Modbus Input) | Read/Write | 0: Disable 1: Enabled | Remote Modbus Start-Enable input. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46348 | Target Speed | Read Only | Multiplier : 0.0625 Offset: 0 Size (bits): 16 Sign: 32 Units: rpm Lower Limit: NA Upper Limit: NA Default: NA | The speed reference function desired speed before ramping | PC 2.x, PC 3.x |
| 46349 | Target Speed | Read Only | Multiplier : 0.0625 Offset: 0 Size (bits): 16 Sign: 32 Units: rpm Lower Limit: NA Upper Limit: NA Default: NA | The speed reference function desired speed before ramping | PC 2.x, PC 3.x |
| 46364 | Modbus Register Read Only Enable | Read Only | 0: Disable 1: Enable | Modbus Register Read Only Enable For TB15 Modbus Communication Port. | PC 2.x, PC 3.x |
| 46365 | Modbus Register Read Only Enable (J14) | Read Only | 0: Disable 1: Enable | Modbus Register Read Only Enable For J14 Modbus Communication Port. | PC 3.x |
| 46366 | Modbus Stop Bits (J14) | Read/Write | 0:01 1:02 | Sets the Modbus number of stop bits for this node Limited to 1 bit if parity = Odd or Even | PC 3.x |
| 46367 | Modbus Bus Message Count (J14) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: Upper Limit: | The number of Modbus messages with no response, for J14 port only | PC 3.x |
| 46368 | Modbus CRC Error Count (J14) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: Upper Limit: | The number of Modbus CRC errors, for J14 only. | PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46369 | Modbus Exception Count (J14) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: Upper Limit: | Modbus exception count, for J14 only. | PC 3.x |
| 46370 | Modbus No Response Count (J14) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: Upper Limit: | Modbus no response count, for J14 only. | PC 3.x |
| 46371 | Modbus Slave Message Count (J14) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: Upper Limit: | The number of Modbus slave messages, for J14 only. | PC 3.x |
| 46372 | Modbus Node Address (J14) | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 8 Sign: U Unit: Lower Limit: 1 Upper Limit: 247 | Sets the Modbus address for this node, for J14 only. | PC 3.x |
| 46373 | Modbus Baud Rate (J14) | Read/Write | 1.6666667 3.375 6.75 | Sets the baud rate for Modbus communications, for J14 only. | PC 3.x |
| 46374 | Modbus Parity (J14) | Read/Write | 0: Even 1: Odd 2: None | Sets the Modbus parity for this node, for J14 only. | PC 3.x |
| 46376 | Modbus Baud Rate | Read/Write | 0: 2400 Baud 1: 4800 Baud 2: 9600 Baud 3: 19200 Baud 4: 38400 Baud | Sets the Modbus baud rate. | PC 2.x, PC 3.x |
| 46377 | Modbus Parity | Read/Write | 0: Even 1: Odd 2: None | Sets the Modbus parity for this node | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46378 | Modbus Node Address | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 8 Sign: U Unit: Lower Limit: 1 Upper Limit: 247 | Sets the Modbus address for this node | PC 2.x, PC 3.x |
| 46379 | Modbus Stop Bits | Read/Write | 0:01 1:02 | Sets the Modbus number of stop bits for this node Limited to 1 bit if parity = Odd or Even | PC 2.x, PC 3.x |
| 46380 | HMI113 Fault 3 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 46381 | HMI113 Fault 3 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 46382 | HMI113 Fault 3 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 46383 | HMI113 Fault 3 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46384 | HMI113 Fault 3 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 46385 | HMI113 Fault 3 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 46386 | HMI113 Fault 3 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 46387 | HMI113 Fault 3 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 46388 | HMI113 Fault 3 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 46389 | HMI113 Fault 3 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46390 | HMI113 Fault 3 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 46391 | HMI113 Fault 3 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 46392 | HMI113 Fault 3 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 46393 | HMI113 Fault 3 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 46394 | HMI113 Fault 3 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 46395 | HMI113 Fault 3 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46396 | HMI113 Fault 3 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 46397 | HMI113 Fault 3 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 46398 | HMI113 Fault 3 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 46399 | HMI113 Fault 3 Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text string to enter the configurable fault text for this fault. | PC 2.x, PC 3.x |
| 46600 | Aux101 0 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46601 | Aux101 0 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46602 | Aux101 0 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46603 | Aux101 0 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46604 | Aux101 0 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46605 | Aux101 0 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46606 | Aux101 0 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46607 | Aux101 0 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46608 | Aux101 0 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46609 | Aux101 0 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46610 | Aux101 0 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46611 | Aux101 0 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46612 | Aux101 0 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46613 | Aux101 0 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46614 | Aux101 0 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46615 | Aux101 0 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46616 | Aux101 0 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46617 | Aux101 0 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46618 | Aux101 0 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46619 | Aux101 0 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46620 | Aux101 0 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46621 | Aux101 0 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46622 | Aux101 0 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46623 | Aux101 0 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46624 | Aux101 0 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46625 | Aux101 0 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46626 | Aux101 0 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46627 | Aux101 0 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46628 | Aux101 0 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46629 | Aux101 0 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46630 | Aux101 0 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46631 | Aux101 0 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46632 | Aux101 0 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46633 | Aux101 0 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46634 | Aux101 0 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46635 | Aux101 0 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46636 | Aux101 0 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46637 | Aux101 0 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46638 | Aux101 0 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46639 | Aux101 0 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46640 | Aux101 1 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46641 | Aux101 1 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46642 | Aux101 1 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46643 | Aux101 1 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46644 | Aux101 1 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46645 | Aux101 1 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46646 | Aux101 1 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46647 | Aux101 1 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46648 | Aux101 1 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46649 | Aux101 1 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46650 | Aux101 1 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46651 | Aux101 1 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46652 | Aux101 1 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46653 | Aux101 1 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46654 | Aux101 1 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46655 | Aux101 1 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46656 | Aux101 1 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46657 | Aux101 1 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46658 | Aux101 1 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46659 | Aux101 1 Input 1 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46660 | Aux101 1 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46661 | Aux101 1 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46662 | Aux101 1 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46663 | Aux101 1 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46664 | Aux101 1 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46665 | Aux101 1 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46666 | Aux101 1 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46667 | Aux101 1 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46668 | Aux101 1 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46669 | Aux101 1 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46670 | Aux101 1 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46671 | Aux101 1 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46672 | Aux101 1 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46673 | Aux101 1 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46674 | Aux101 1 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46675 | Aux101 1 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46676 | Aux101 1 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46677 | Aux101 1 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46678 | Aux101 1 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46679 | Aux101 1 Input 2 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46800 | Aux101 0 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46801 | Aux101 0 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46802 | Aux101 0 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46803 | Aux101 0 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46804 | Aux101 0 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46805 | Aux101 0 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46806 | Aux101 0 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46807 | Aux101 0 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46808 | Aux101 0 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46809 | Aux101 0 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46810 | Aux101 0 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46811 | Aux101 0 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46812 | Aux101 0 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46813 | Aux101 0 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46814 | Aux101 0 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46815 | Aux101 0 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46816 | Aux101 0 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46817 | Aux101 0 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46818 | Aux101 0 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46819 | Aux101 0 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46820 | Aux101 0 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46821 | Aux101 0 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46822 | Aux101 0 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46823 | Aux101 0 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46824 | Aux101 0 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46825 | Aux101 0 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46826 | Aux101 0 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46827 | Aux101 0 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46828 | Aux101 0 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46829 | Aux101 0 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46830 | Aux101 0 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46831 | Aux101 0 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46832 | Aux101 0 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46833 | Aux101 0 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46834 | Aux101 0 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46835 | Aux101 0 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46836 | Aux101 0 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46837 | Aux101 0 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46838 | Aux101 0 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46839 | Aux101 0 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46840 | Aux101 0 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46841 | Aux101 0 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46842 | Aux101 0 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46843 | Aux101 0 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46844 | Aux101 0 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46845 | Aux101 0 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46846 | Aux101 0 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46847 | Aux101 0 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46848 | Aux101 0 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46849 | Aux101 0 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46850 | Aux101 0 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46851 | Aux101 0 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46852 | Aux101 0 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46853 | Aux101 0 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46854 | Aux101 0 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46855 | Aux101 0 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46856 | Aux101 0 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46857 | Aux101 0 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46858 | Aux101 0 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46859 | Aux101 0 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46860 | Aux101 0 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46861 | Aux101 0 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46862 | Aux101 0 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46863 | Aux101 0 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46864 | Aux101 0 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46865 | Aux101 0 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46866 | Aux101 0 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46867 | Aux101 0 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46868 | Aux101 0 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46869 | Aux101 0 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46870 | Aux101 0 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46871 | Aux101 0 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46872 | Aux101 0 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46873 | Aux101 0 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46874 | Aux101 0 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46875 | Aux101 0 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46876 | Aux101 0 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46877 | Aux101 0 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46878 | Aux101 0 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46879 | Aux101 0 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46880 | Aux101 1 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46881 | Aux101 1 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46882 | Aux101 1 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46883 | Aux101 1 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46884 | Aux101 1 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46885 | Aux101 1 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46886 | Aux101 1 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46887 | Aux101 1 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46888 | Aux101 1 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46889 | Aux101 1 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46890 | Aux101 1 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46891 | Aux101 1 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46892 | Aux101 1 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46893 | Aux101 1 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46894 | Aux101 1 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46895 | Aux101 1 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46896 | Aux101 1 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46897 | Aux101 1 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46898 | Aux101 1 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46899 | Aux101 1 Input 3 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46900 | Aux101 1 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: Unit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46901 | Aux101 1 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46902 | Aux101 1 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46903 | Aux101 1 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46904 | Aux101 1 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46905 | Aux101 1 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46906 | Aux101 1 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46907 | Aux101 1 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46908 | Aux101 1 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46909 | Aux101 1 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46910 | Aux101 1 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46911 | Aux101 1 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46912 | Aux101 1 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46913 | Aux101 1 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46914 | Aux101 1 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46915 | Aux101 1 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46916 | Aux101 1 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46917 | Aux101 1 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46918 | Aux101 1 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46919 | Aux101 1 Input 4 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46920 | Aux101 1 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46921 | Aux101 1 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46922 | Aux101 1 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46923 | Aux101 1 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46924 | Aux101 1 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46925 | Aux101 1 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46926 | Aux101 1 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46927 | Aux101 1 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46928 | Aux101 1 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46929 | Aux101 1 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46930 | Aux101 1 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46931 | Aux101 1 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46932 | Aux101 1 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46933 | Aux101 1 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46934 | Aux101 1 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46935 | Aux101 1 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46936 | Aux101 1 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46937 | Aux101 1 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46938 | Aux101 1 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46939 | Aux101 1 Input 5 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46940 | Aux101 1 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46941 | Aux101 1 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46942 | Aux101 1 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46943 | Aux101 1 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46944 | Aux101 1 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46945 | Aux101 1 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46946 | Aux101 1 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46947 | Aux101 1 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46948 | Aux101 1 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46949 | Aux101 1 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46950 | Aux101 1 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46951 | Aux101 1 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46952 | Aux101 1 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46953 | Aux101 1 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46954 | Aux101 1 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46955 | Aux101 1 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46956 | Aux101 1 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46957 | Aux101 1 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46958 | Aux101 1 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46959 | Aux101 1 Input 6 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46960 | Aux101 0 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46961 | Aux101 0 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46962 | Aux101 0 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46963 | Aux101 0 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46964 | Aux101 0 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46965 | Aux101 0 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46966 | Aux101 0 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46967 | Aux101 0 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46968 | Aux101 0 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46969 | Aux101 0 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46970 | Aux101 0 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46971 | Aux101 0 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46972 | Aux101 0 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46973 | Aux101 0 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46974 | Aux101 0 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46975 | Aux101 0 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46976 | Aux101 0 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46977 | Aux101 0 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46978 | Aux101 0 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46979 | Aux101 0 Input 7 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46980 | Aux101 0 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46981 | Aux101 0 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46982 | Aux101 0 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46983 | Aux101 0 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46984 | Aux101 0 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46985 | Aux101 0 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46986 | Aux101 0 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46987 | Aux101 0 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46988 | Aux101 0 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46989 | Aux101 0 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46990 | Aux101 0 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46991 | Aux101 0 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46992 | Aux101 0 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46993 | Aux101 0 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 46994 | Aux101 0 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46995 | Aux101 0 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46996 | Aux101 0 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46997 | Aux101 0 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46998 | Aux101 0 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |
| 46999 | Aux101 0 Input 8 Fault Text | Read/Write | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: C Unit: Lower Limit: Upper Limit: | Twenty (20) character text field to allow for the entry of the displayed configurable fault text. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 47002 | GK1 (60Hz) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | The governor 60Hz K1 gain adjust. | PC 2.x, PC 3.x |
| 47003 | GK2 (60Hz) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 168 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | The governor 60Hz integral gain adjust. | PC 2.x, PC 3.x |
| 47004 | GK3 (60Hz) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | The governor 60Hz K3 gain adjust. | PC 2.x, PC 3.x |
| 47005 | Governor Damping Effect (60Hz) | Read Only | Multiplier: 1.52587890625E- 05 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0.6 Upper Limit: 0.95 | The governor 60Hz damping adjust. | PC 2.x, PC 3.x |
| 47006 | GK1 (50Hz) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | The governor 50Hz K1 gain adjust. | PC 2.x, PC 3.x |
| 47007 | GK2 (50Hz) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | The governor 50Hz integral gain adjust. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 47008 | GK3 (50Hz) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | The governor 50Hz K3 gain adjust. | PC 2.x, PC 3.x |
| 47009 | Governor Damping Effect (50Hz) | Read Only | Multiplier: 1.52587890625E–05 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0.6 Upper Limit: 0.95 | The governor 50Hz damping adjust. | PC 2.x, PC 3.x |
| 47010 | GK1(Idle) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | This trim is used to adjust gk1 in idle mode. | PC 2.x, PC 3.x |
| 47011 | GK2(Idle) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | This trim is used to adjust gk2 in idle mode. | PC 2.x, PC 3.x |
| 47014 | Gain Windowing Enable | Read Only | 0: Disable 1: Enable | Either enables or disables Gain Windowing feature. | PC 2.x, PC 3.x |
| 47015 | GK1 Low(50Hz) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | The governor 50Hz K1 low gain adjust. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 47016 | GK1 Low(60Hz) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | The governor 60Hz K1 low gain adjust. | PC 2.x, PC 3.x |
| 47017 | GK1 High(50Hz) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | The governor 50Hz K1 high gain adjust. | PC 2.x, PC 3.x |
| 47018 | GK1 High(60Hz) | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 0 Upper Limit: 65530 | The governor 60Hz K1 high gain adjust. | PC 2.x, PC 3.x |
| 47019 | Governor Speed Delta High | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 50 Upper Limit: 1000 | The speed error higher limit. | PC 2.x, PC 3.x |
| 47020 | Governor Speed Delta Low | Read Only | Multiplier: 1 Offset: 0 Size (bits): 16 Sign: U Unit: Lower Limit: 50 Upper Limit: 1000 | The speed error lower limit. | PC 2.x, PC 3.x |
| 47021 | Intake Manifold Temperature Sensor Type | Read Only | 0: PGBU 1: EBU | Either PGBU(Onan) or EBU(Cummins) sensor. | PC 2.x, PC 3.x |
| 47022 | Intake Manifold Temperature Sensor Enable | Read Only | 0: Disable 1: Enable | Intake Manifold Temperature Sensor available or not. | PC 2.x, PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 47023 | Oil Temperature Sensor Type | Read Only | 0: PGBU 1: EBU | Either PGBU(Onan) or EBU(Cummins) sensor. | PC 2.x, PC 3.x |
| 47024 | Oil Temperature Sensor Enable | Read Only | 0: Disable 1: Enable | High Oil Temperature Sensor available or not. | PC 2.x, PC 3.x |
| 47025 | AVR PWM Command | Read Only | Multiplier: 0.01 Offset: 0 Size (bits): 16 Sign: U Unit: % Lower Limit: Upper Limit: | The AVR PWM software command. Linear relationship between counts and % duty cycle with 10000 counts=100% duty cycle. | PC 2.x, PC 3.x |
| 47026 | Coolant Temperature 2 Enable | Read Only | 0: Disable 1: Enable | Coolant Temperature 2 Enable | PC 3.x |
| 47027 | Start Inhibit Delay Progress | Read Only | Multiplier : 0.05 Offset: 0 Size (bits): 16 Sign: U Units: Seconds Lower Limit: NA Upper Limit: NA Default: NA | Delay progress until a fault is declared for start inhibit | PC 3.x |
| 47028 | Genset Voltage Sensing MCB status | Read Only | 0: Close 1: Open 2: Reserved 3: N/A 4: Network Failure | Indicates the Genset Voltage sensing MCB status. | PC 3.x |
| 47029 | Customer Gas Valve Status | Read Only | 0: Open 1: Closed 2: Reserved 3: N/A 4: Network Failure | Indicates the status of the Customer Gas Valve position. | PC 3.x |
| 47030 | Crankcase Pressure Extended | Read Only | Multiplier : 0.01 Offset: 0 Size (bits): 16 Sign: S Units: psi Lower Limit: -35.67 Upper Limit: 38 Default: NA | Monitor point for the Crankcase Pressure with extended precision. | PC 2.x PC 3.x |

| Addr. | Parameter | Access | Specifications | Description | Control |
| --- | --- | --- | --- | --- | --- |
| 47032 | HT Coolant Inlet Temperature | Read Only | Multiplier: 0.1 Offset: 0 Size (Bits): 16 Sign: S Unit: Deg.F Lower Limit: NA Upper Limit: NA | HT Coolant Inlet Temperature | PC 3.x |
| 47033 | Engine Turbocharger 1 Compressor Intake Temperature | Read Only | Multiplier: 0.1 Offset: 0 Size (Bits): 16 Sign: S Unit: Deg.F Lower Limit: 273 Upper Limit: 1734.968 | Intake temperature of engine turbocharger 1 compressor. | PC 3.x |
| 47034 | Gas Methane Percentage Raw Input (Modbus) | Read write | Multiplier: 1 Offset: 0 Size (Bits): 16 Sign: U Unit: Percentage Lower Limit: 0 Upper Limit: 1000 | Raw count value of methane content present in the natural gas used for LBNG genset | PC 3.x |
| 47050 | Intake Manifold Temp. Rate of Change Threshold | Read write | Multiplier: 0.1 Unit: Deg.F/Seconds | Threshold to decide the Intake Manifold Backfire condition, Value entered is for Deg.F/Seconds, Deg.F/2 Seconds is obtained by a scalar of 2 in PCC software. | PC 3.x |
| 47051 | Gas Temperature | Read Only | Multiplier: 0.1 Offset: 0 Size (Bits): 16 Sign: S Unit: Deg.F Lower Limit: NA Upper Limit: NA | This parameter is to display engine gas fuel temperature. | PC 3.x |
| 47052 | Turbocharger Wastegate Position | Read Only | Multiplier: 0.1 Offset: 0 Size (Bits): 16 Sign: U Unit: Percentage Lower Limit: 0 Upper Limit: 100 | To display engine turbocharger wastegate position. | PC 3.x |